## Complete Report
Overall System Condition Spreadsheet- BWSD
Line Condition Category | [24 empty] | Annual Maintenance Action
KEYS
| ABBREVIATION KEY |  |  | CONDITIONS KEY
| CIP- CURED IN PLACE |  |  |  |  | INFILTRATION |  | BROKEN | JOINTS | ROOTS | SAGS | DEBRIS | CRACKS | DETERIORATION | [6 empty] | Lines Complete | Percentage | Linear Feet
| CI- CAST IRON |  |  | NONE |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 521 | 98.49% | 102351.37
| CO - CONCRETE |  |  | LIGHT |  | 20 |  | 20 | 10 | 10 | 10 | 10 | 10 | 10 | [11 empty] | H1- HOT SPOT: ANNUAL VIDEO/JET
| DI- DUCTILE IRON |  |  | MODERATE |  | 50 |  | 50 | 25 | 25 | 20 | 20 | 20 | 20 | [5 empty] | Still Needs Assessed |  | Percentage | Linear Feet |  |  | H2- HOT SPOT: VIDEO/JET EVERY 6 MONTHS
| P.E. - POLYETHYLENE |  |  | EXTENSIVE |  | 100 |  | 100 | 50 | 50 | 40 | 40 | 40 | 30 | [5 empty] | 8 |  | 1.512% | 911.21 |  |  | H/RC- HOT SPOT/ROOT CUT: VIDEO/JET EVERY YEAR//ROOT CUT EVERY 3 YEARS
| PVC - PLASTIC | [24 empty] | H/RC (H/RC1= YEAR 1 ROOT CUT, H/RC2= YEAR 2 ROOT CUT, H/RC3= YEAR 3 ROOT CUT)
| RL- RIB-LOC |  |  | EMERGENCY RANK: |  | 151+ | 1-REPAIR IMMEDIATELY |  |  | 100-150 |  | 2- REPAIR NEEDED/MONITOR ANNUALLY | [13 empty] | RC: ROOT CUT
| SL- SLIP-LINE | [19 empty] | PERCENTAGE |  | LINEAR FEET |  |  | RC (RC1= YEAR 1 ROOT CUT, RC2= YEAR 2 ROOT CUT, RC3= YEAR 3 ROOT CUT)
| ST- STUB/NO UPSTREAM ACCESS |  |  | SCORE: |  |  | 0-25 | OVERALL GOOD CONDITION | [6 empty] | CATEGORY 1 |  | GREEN |  |  |  | 63% |  | 64482.27 |  |  | REG: JET/VIDEO EVERY 3 YEARS
| VCP - CLAY | [5 empty] | 26-50 | OVERALL FAIR CONDITION | [6 empty] | CATEGORY 2 |  | YELLOW |  |  |  | 25.54% |  | 26142.6 |  |  | REG (REG1= YEAR 1 , REG2= YEAR 2, REG3= YEAR 3)
[7 empty] | 51-75 | OVERALL MODERATE CONDITION | [6 empty] | CATEGORY 3 |  | BLUE |  |  |  | 8.006% |  | 8194
[7 empty] | 76-100 | REPAIRS SHOULD BE SCHEDULED | [6 empty] | CATEGORY 4 |  | PURPLE |  |  |  | 3.451% |  | 3532.5
[7 empty] | 101+ | EMERGENCY |  | (DEPENDING ON NOTES) |  |  |  |  | CATEGORY 5 |  | RED |  |  |  | 0%
| STREET | MAP | MH | TO | MH | LENGTH | VIDEO FEET | SIZE | TYPE | SLOPE | LAST VIDEO | % FULL | INFILTRATION | BROKEN | JOINTS | ROOTS | SAGS | DEBRIS | CRACKS | DETERIORATION | TAPS | CAPPED TAPS | EMERGENCY RANK | OVERALL SCORE | MAINTENANCE ACTION | OPERATOR NOTES AND CAPITAL IMPROVEMENTS | YEAR INSTALLED | AGE
1 | EASEMENT | M-8 | STUB |  | S-28B | 5 | 5 | 8 | PVC | - | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
2 | EASEMENT | M-8 | S-28B |  | S-28A | 185 | 183.8 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 3 | 0 | 0 | 20 | REG2 | Some sagging throughout L, some joints throughout egging/deformed L | -
3 | EASEMENT | M-8 | S-28A |  | S-28 | 300 | 300.7 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 10 | REG2 | Some joints throughout egging/deformed L | -
4 | EASEMENT | M-8 | STUB |  | S-28 | 5 | 4 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
5 | SHERIDAN FRONTAGE RD | M-8 | S-28 |  | S-27 | 182 | 180.1 | 8 | PVC | - | 2023 | 5-10% | 20 | 0 | 10 | 0 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 50 | REG2 | Sag 153-170.5 M. Material change: VCP 170.5. Joint offset 169.8 L. Possible infil in tap L. | -
6 | SHERIDAN FRONTAGE RD | M-8 | S-27 |  | S-26 | 320 | 315.7 | 8 | VCP | 0.78% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1982 | 42
7 | EASEMENT | M-8 | S-26 |  | S-25 | 34 | 38.1 | 8 | VCP | 0.4% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1982 | 42
8 | EASEMENT | M-8 | S-25 |  | S-24 | 287 | 286.6 | 8 | VCP | 0.4% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1982 | 42
9 | EASEMENT | M-8 | S-24 |  | S-23 | 48 | 45 | 8 | VCP | 0.4% | 2023 | 5% | 20 | 0 | 0 | 0 | 10 | 20 | 10 | 0 | 0 | 0 | 0 | 60 | REG2 | OUTSIDE DROP 41.5. Lot of grit in line M, possible sag 0-16 L, possible crack with infill on other side of drop L, possible infil in drop at joint L. | 1982 | 42
10 | EASEMENT | M-8 | S-23 |  | S-22 | 37 | 38.4 | 8 | VCP | 2% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 20 | REG2 | UPSTREAM// Circumferential crack 5 L. Deposits/encrustation on bottom of pipe 31 L. | 1982 | 42
11 | RALSTON FRONTAGE RD | M-8 | S-22C |  | S-22B | 74 | 71.4 | 8 | VCP | - | 2023 | - | 20 | 0 | 0 | 0 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 60 | REG2 | 19.4 multiple fracture w/deposits and infil stain L, infil: dripper 26.6 L. Sag: 32-39 L, 50-59 L. Deterioration/pitting thorughout L. Infil stain around joint 42.4 L. Nothing upstream and no taps in line: Could probably be plugged or abandoned. | -
12 | RALSTON FRONTAGE RD | M-8 | S-22B |  | S-22A | 246 | 245.9 | 8 | VCP | - | 2023 | 5% | 50 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 3 | 0 | 0 | 70 | REG2 | Sag through out 23-154 L. Deposits/encrustation throughout L. Infil: runner in joint 94.4 M, 104.7 L. Infil stain 28.5 L. | -
13 | RALSTON FRONTAGE RD | M-8 | S-22A |  | S-22 | 235 | 251.1 | 8 | VCP | - | 2023 | 5% | 20 | 0 | 0 | 0 | 10 | 10 | 0 | 10 | 2 | 0 | 0 | 50 | REG2 | Infil: Gusher in tap 8 E, possible infil gusher in tap 80.8 E, infil: weeper238.7 L. Sags throughout L, debris/encrustation throughout L, deterioration througout L. Longitudinal crack 87.5 L, Longitudinal crack 151.2 L w/ infil stain L. | -
14 | EASEMENT | M-8 | S-22 |  | S-21 | 240 | 273.7 | 10 | VCP | - | 2023 | 5% | 20 | 0 | 0 | 0 | 0 | 10 | 20 | 0 | 1 | 0 | 0 | 50 | REG2 | 58.7 ENCRUSTATION L, 71.1 INFILL STAIN L, 93.6 ENCRUSTATION L, 128 CRACK SPIRL GOES ALONG BOTTOM OF MAIN COULD BE EXFILLTRATION M, 159.8 ENCRUSTATION M, 196.6 CRACK CIRCUM L. Infil stain at joint 49 L, 178.3 L, 226.4 L, 261.2 L. | -
15 | EASEMENT | M-8 | S-21 |  | S-19 | 285 | 238.6 | 10 | DIP | 0.3% | 2023 | 5-20% | 20 | 0 | 0 | 0 | 20 | 10 | 0 | 10 | 0 | 0 | 0 | 60 | REG2 | SAG 92-127.5 M. Deposits/encrustation thorughout L, and deterioration L. Hard to tell but may have some infil stains at joints: 31.6 for example L. | -
16 | EASEMENT | L-8 | S-19 |  | S-18 | 34 | 33.9 | 10 | PVC | 0.27% | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
17 | SHERIDAN BLVD | L-8 | S-18 |  | S-17 | 140 | 141.3 | 10 | CIP | 0.22% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
18 | EASEMENT | L-7 | S-17 |  | S-16 | 152 | 149.2 | 12 | P.E. | 0.22% | 2023 | 10% | 20 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | REG2 | 9.5 INFILL WEAPER L, 22.3 INFILL WEAPER L, Point repair: PVC 53.4-78.2 w/offset joint L. g | -
19 | EASEMENT | L-7 | S-16 |  | S-15 | 336 | 337.7 | 12 | PVC | 0.2% | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 30 | REG2 | Some sagging throughout L, some joints throughout egging/deformed L, debris/encrustation throughout L | -
20 | EASEMENT | L-7 | S-15 |  | S-14 | 260 | 259.3 | 12 | PVC | 0.2% | 2023 | 5% | 0 | 0 | 25 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 45 | REG2 | LOOKS LIKE FAT/GREASE HAS STUCK TO THE SIDES THROUGH OUT THE VIDEO. SAG 190-238 L. Egging joints thoughout L except: 88.2 M, 100 M, 111.6 M, 123.4 M, 147 M, 177.9 M, 220.9 M. | -
21 | EASEMENT | L-7 | S-14 |  | S-13 | 346 | 345.1 | 12 | PVC | 0.2% | 2023 | 5-15% | 0 | 0 | 25 | 0 | 20 | 10 | 0 | 0 | 0 | 0 | 0 | 55 | REG2 | SAG 65-73 L, SAG 81-103 L, SAG 113-130 L, SAG 262-343 M. THERE IS A LOT OF GRIT/SAND THROUGH THE MAIN. Egging joints throughout L Except: 81.5 M, 93.3 M, 112.5 M, 131.7 M, 304.1 M. | -
22 | EASEMENT | L-7 | S-13 |  | S-12 | 390 | 392 | 12 | DIP | 0.2% | 2023 | 5% | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 20 | REG2 | Sag: 201-391 (end) L, surface damage/corrosion throughout L | -
23 | W 53RD AVE | L-8 | S-12S |  | S-12R | 152 | 151.2 | 8 | VCP | 0.4% | 2023 | 5-10% | 0 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 2 | 0 | 0 | 20 | REG2 | UPSTREAM: Sag 126-132 L. Circuferential crack 111.8 L. | -
24 | W 53RD AVE | L-8 | S-12R |  | S-12Q | 285 | 283 | 8 | VCP | 0.36% | 2023 | 5-15% | 0 | 0 | 0 | 0 | 20 | 0 | 10 | 10 | 1 | 0 | 0 | 40 | REG2 | Sag 30-72 M, 228-256 M. Circumferential crack 180.4 L. Pitting/deterioration throughout L | -
25 | W 53RD AVE | L-8 | S-12Q |  | S-12P | 215 | 216.3 | 8 | VCP | 0.36% | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
26 | W 53RD AVE | L-8 | S-12P-1 |  | S-12P | 248 | 246.8 | 8 | CIP | 0.4% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | Lined in 2023. | -
27 | W 53RD AVE | L-8 | S-12P |  | S-12N | 205 | 213 | 8 | VCP | 0.36% | 2023 | 15% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
28 | EASEMENT | L-8 | S-12N |  | S-12M | 267 | 265.7 | 10 | VCP | 0.3% | 2023 | 10% | 50 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 70 | REG2 | 248.1 CRACK LONG W/INFILL WEEPER L, 251.1 CRACK MULTIPLE M & INFILL WEEPER/Runner L, 256.1 FRACTURE LONGITUDE M, 260.5 INFILL WEEPER L, 262.6 CRACK MULT M, INFILL THROUGH OUT PIPE. | -
29 | EASEMENT | L-8 | S-12M |  | S-12L | 275 | 274.6 | 10 | PVC | 0.26% | 2023 | 10-40% | 0 | 0 | 25 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | REG2 | 21-30 SAG L, 33-65 SAG M, 36.8 EGGING M, 155-208 SAG L. Sag: 73-131 L, 225-266 L. Egging joints/out of round throughout pipe L-M | 1991 | 33
30 | EASEMENT | L-8 | S-12L |  | S-12K | 56 | 58 | 10 | VCP | 0.3% | 2023 | 5-10% | 20 | 0 | 25 | 0 | 10 | 10 | 10 | 0 | 0 | 0 | 0 | 75 | REG2 | UPSTREAM: AT 5.3 IN COULD NOT PASS OFF SET. DOWNSTREAM VIDEO; ABANDON VIDEO AT 51’ OFFSET M. Sealing ring in the beginning of pipe/obstruction but they were able to get around it. Crack with infil stain at top of pipe 2.5 L, joint with infil stain/deposits L & crack L, infil stain at point repair 51.7 L. Sag 9-33 L. Point repair: PVC 51.7- end MH | -
31 | EASEMENT | L-8 | S-12K |  | S-12J | 357 | 346.6 | 12 | PVC | 0.48% | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG2 | Joints throughout egging/deformed L, sags throughout L | -
32 | EASEMENT | L-8 | S-12J |  | S-12I | 350 | 347.1 | 12 | PVC | 0.48% | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 30 | REG2 | Debris/encrustation througout L, joints throughout egging/deformed L, sags throughout L | -
33 | EASEMENT | L-8 | S-12I |  | S-12H | 158 | 158.1 | 12 | PVC | 0.48% | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 1 | 0 | 0 | 20 | REG2 | MH 158’ W/INFILL AT LATTER END (MH lined in 2023). Joints egging/out of round throughout pipe L. Sag 62-133 L. | -
34 | EASEMENT | L-8 | S-12H |  | S-12G | 150 | 149.8 | 12 | PVC | 0.48% | 2023 | 5-10% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG2 | Sags: 23-43 L, 133-149 (end)M. Joints throughout egging/deformed L | -
35 | SHERIDAN BLVD | L-8 | S-12G |  | S-12F | 143 | 143.1 | 12 | DIP | 0.3% | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | REG2 | Corrosion thorughout L | -
36 | W 54TH AVE | L-7 | S-12F-3 |  | S-12F-2 | 237 | 236.7 | 8 | CIP | 0.4% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | Surchage from downstream/downstream is flat line that "backs up" into the end of this line. | 1976 | 48
37 | W 54TH AVE | L-7 | S-12F-2 |  | S-12F-1 | 112 | 111.5 | 8 | CIP | 0.4% | 2023 | 15% | 50 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | REG2 | Infil: weeper 76.5 M. Sag: 27-52 L, 82-102 E. | 1976 | 48
38 | EASEMENT | L-7 | S-12F-1 |  | S-12F | 90 | 90 | 8 | P.E. | 0.4% | 2023 | 10% | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | REG2 | 73 SEAL IS COMING LOOSE L. Was originally a drop MH but drop wasn't cut out when pipe burst was done. | -
39 | EASEMENT | L-7 | S-12F |  | S-12E | 155 | 155.6 | 12 | PVC | 0.62% | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 20 | REG2 | UPSTREAM: DIP 94 TO END W/CROSION M | -
40 | EASEMENT | L-7 | S-12E |  | S-12D | 314 | 316 | 12 | PVC | 0.45% | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG2 | Some sagging throughout L, some joints throughout egging/deformed L | -
41 | EASEMENT | L-7 | S-12D |  | S-12C | 383 | 385 | 12 | PVC | 0.45% | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG2 | Some sagging throughout L, some joints throughout egging/deformed L | -
42 | EASEMENT | L-7 | S-12C |  | S-12B | 297 | 295.3 | 12 | VCP | 0.45% | 2023 | 10-15% | 0 | 0 | 0 | 0 | 20 | 0 | 10 | 0 | 0 | 0 | 0 | 30 | REG2 | 127.4-140 SAG M, FRACTURE CIRC. 187.1. Sag: 0-45 L, 184-201 L, 268-289 L. Crack at top of pipe 0 L, 22.4 L, 28.7 L, 206.1 L, 247.6 L. Circumferential crack 120.3 L, 126.1 L, 185.6 L, 274.4 L. Camera was having some problems getting through: grit? | -
43 | EASEMENT | L-7 | S-12B |  | S-12A | 123 | 121.9 | 12 | VCP | 0.39% | 2023 | 10% | 0 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 20 | REG2 | ALL JOINTS ARE CRACKED CIRC L, GOOD PIPE TO HAVE LINED. Sag: 43-56 L, 72-121 L. Crack near joint 13.8 L, 53.4 L, 87.2 L | -
44 | EASEMENT | L-7 | S-12A |  | S-12 | 249 | 248.5 | 12 | VCP | 0.33% | 2023 | 10% | 50 | 0 | 10 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 80 | REG2 | CRACK L W/INFILL 2.3RUNNER M, Point repair: PVC 24-39.5, EVERY JOINT IS CRACKED GOOD PIPE FOR LINNING. Sags throughout L. Crack at the top of pipe near joint 79L, 212.1 L | -
45 | EASEMENT | L-7 | S-12 |  | S-11 | 278 | 279.1 | 12 | VCP | 0.22% | 2023 | 10% | 50 | 0 | 10 | 0 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 100 | REG2 | 198’ INFILL RUNNER M. Sealing rings in a lot of joints look worn or are coming out of the joint L. Sags: 50-92 L, 154-261 L. Deposits/encrustation attached throughout pipe L. Deterioration? side of pipe looks rough 150.2 L. Crack at top of pipe near joint 183.4 L, 203.3 L, circumferential crack 275 L. | 1973 | 51
46 | EASEMENT | L-7 | S-11 |  | S-10 | 399 | 398.1 | 12 | PVC | 0.22% | 2023 | 10% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG2 | FROM 0-128 SAG L, SAG 160-179. Egging/out of round joints throughout L | 1973 | 51
47 | EASEMENT | L-7 | S-10 |  | S-9 | 217 | 217.3 | 12 | VCP | 0.22% | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | REG2 | .7 CRACK CIRC L, EVERY JOINT IS CRACKED RECOMMEND CURE IN PLACE | 1973 | 51
48 | EASEMENT | L-7 | S-9 |  | TN-1 | 258 | 257.1 | 15 | P.E. | 0.2% | 2023 | 5-10% | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | REG2 | 5.2-59 SAG L. Sag: 85-104 L, 145-203 L, 223-257 L | 1973 | 51
49 | TENNYSON ST | L-7 | TN-1 |  | TN-2 | 90 | 86 | 15 | VCP | 0.4% | 2023 | 10% | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG2 | UPSTREAM: 82 INFILL WEEPER L | 1973 | 51
50 | STUART ST | L-6 | ST-5 |  | ST-4 | 42 | 39.8 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
51 | STUART ST | L-6 | ST-4 |  | ST-3 | 65 | 62.7 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 0 | REG2 | NO COMMENTS | -
52 | STUART ST | L-6 | ST-3 |  | ST-2 | 340 | 340.5 | 8 | VCP | 4.4% | 2023 | 5% | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 10 | H/RC2 | Roots thorughout L | -
53 | STUART ST | L-6 | ST-2 |  | ST-1 | 138 | 141.3 | 8 | VCP | 4.32% | 2023 | 5% | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 3 | 0 | 0 | 20 | REG2 | Roots 11 L, 16 L, 21.6 L.2.2. Circumferential fracture L. | -
54 | W 53RD AVE | L-6 | ST-1 |  | TN-6 | 335 | 333.6 | 8 | PVC | 4.5% | 2023 | 5% | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 4 | 0 | 0 | 20 | REG2 | MATERIAL CHANGE TO DIP 224.5-242.3 Corrosion L. Egging joints: 78.8 L, 194.9 L, 290.4 L, | -
55 | TENNYSON ST | L-6 | TN-11 |  | TN-10 | 180 | 179.8 | 8 | PVC | 4% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | 1988 | 36
56 | TENNYSON ST | L-6 | TN-10 |  | TN-9 | 20 | 18.3 | 8 | VCP | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
57 | W 52ND PL | L-7 | TN-9A |  | TN-9 | 294 | 293.9 | 8 | VCP | 0.4% | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 0 | 10 | 10 | 6 | 5 | 0 | 40 | RC2 | BROKEN JOINT 72.7 L, 154 CRACK LONG L. Most of the joints are offset/out of alignment L. Sag: 40-53 L, 64-86 L, 111-146 L, 153-165 L, 171-186 L, 245-257 L. Deterioration/pitting throughout L. | -
58 | TENNYSON ST | L-6 | TN-9 |  | TN-8 | 260 | 246.3 | 8 | VCP | - | 2023 | 5% | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | 4 | 3 | 0 | 20 | RC2 | POINT REPAIR: PVC 121.9-125.5, 243.2 ROOTS L. Deterioration/pitting through out L. | -
59 | EASEMENT | L-7 | RP-3.4 |  | RP-3.3 | 239 | 236.2 | 8 | PVC | 0.65% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1999 | 25
60 | EASEMENT | L-7 | RP-3.3 |  | RP-3.2 | 67 | 67.2 | 8 | PVC | 0.44% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1999 | 25
61 | EASEMENT | L-7 | RP-3.2 |  | RP-3.1 | 90 | 91.3 | 8 | PVC | 0.94% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1999 | 25
62 | EASEMENT | L-7 | RP-3.1 |  | RP-3 | 174 | 173.3 | 8 | PVC | 1.07% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1999 | 25
63 | EASEMENT | L-7 | STUB |  | RP-6 | 5 | 5 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | H1 | UPSTREAM//NO COMMENTS (televising didn't go to tap but it can be seen from MH) | -
64 | EASEMENT | L-7 | RP-6 |  | RP-5 | 248 | 244.7 | 8 | PVC | 0.36% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 0 | H1 | UPSTREAM//NO COMMENTS | 1999 | 25
65 | EASEMENT | L-7 | RP-5 |  | RP-4 | 42 | 41.9 | 8 | PVC | 0.4% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1999 | 25
66 | EASEMENT | L-7 | RP-4 |  | RP-3 | 138 | 139.3 | 8 | PVC | 0.44% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1999 | 25
67 | EASEMENT | L-7 | RP-3 |  | RP-2 | 32 | 32 | 8 | PVC | 0.71% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1999 | 25
68 | EASEMENT | L-7 | RP-2 |  | RP-1 | 170 | 168.2 | 8 | PVC | 0.42% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1999 | 25
69 | EASEMENT | L-7 | RP-1 |  | TN-8C | 50 | 46.1 | 8 | PVC | 0.24% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1999 | 25
70 | EASEMENT | L-7 | TN-8C |  | TN-8B | 240 | 237.5 | 8 | VCP | 0.4% | 2023 | 5% | 0 | 0 | 10 | 10 | 20 | 0 | 10 | 10 | 1 | 0 | 0 | 60 | RC2 | Roots in joint: 25.7 L, 35.9 L, 56 L, 61.2 L, 86.5 L, 96.6 L, 111.7 L, 137 L, 162 L, 187.6 L, 192.7 L, 207.9 L, 228.1 L. Broken Joint 51.1 L possibly seperated. Sag: 5-36 L, 50-56 L, 67-82 L, through out 94-235 L/M. Deterioration at joint 17.9 L, 30.2 L, 172.2 L. Pitting/deterioration 151.1 L. Buldge in pipe or crack at top 2 side 127 L, 129.5 L. Crack at top of pipe 218.1 L. | -
71 | EASEMENT | L-7 | TN-8B |  | TN-8A | 87 | 85.9 | 8 | CIP | 0.4% | 2023 | 5-10% | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG2 | Sag 28-85 M. Lined in 2023 after video. | -
72 | ST CLAIR PL | L-7 | TN-8A |  | TN-8 | 258 | 255.8 | 8 | VCP | 0.4% | 2023 | 5-15% | 0 | 20 | 0 | 10 | 20 | 0 | 10 | 10 | 0 | 0 | 0 | 70 | RC2 | CRACK 2 CIRC L, 4.6 Break W/ROOTS L, ENCRUSTATION 62-79, 204.2 ROOTS IN JOINT L, SAG 229-255.8 M. Roots in joint: 71.6 L. Sag: 13.8-21 L, 25-52 L, 56-72 L, 94-102 L, 127-153 L, 188-199 L, 218-225 L. Buldge in side of pipe w/crack 163.1 L, 165.8 L | -
73 | TENNYSON ST | L-7 | TN-8 |  | TN-7 | 55 | 58 | 8 | PVC | 10.47% | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG2 | NO COMMENTS | 2003 | 21
74 | TENNYSON ST | L-7 | TN-7 |  | TN-6 | 80 | 79 | 8 | VCP | 6.72% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 1 | 0 | 0 | 10 | REG2 | Deposits attached/encrustation 63-78 L. | -
75 | TENNYSON ST | L-7 | TN-6 |  | TN-5 | 50 | 55.1 | 8 | VCP | 6.72% | 2023 | 5% | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 10 | 0 | 0 | 0 | 50 | REG2 | ENCRUSTATION 0-49.4 M. Point Repair: PVC 45.7-49.4. Possible infil bottom of joint: 9.2 L, 39.5 L. Deterioration in the drop at the joint L. | -
76 | TENNYSON ST | L-7 | TN-5 |  | TN-4 | 348 | 348.4 | 8 | VCP | 7% | 2023 | 5% | 20 | 0 | 0 | 10 | 0 | 10 | 10 | 10 | 2 | 0 | 0 | 60 | RC2 | ENCRUSTATION 0-65 L. Roots in joint: 288.9 L. Encrustation 336-346 L. Crack: 81.6 L, 106.3 L, 146.7 L, 161.8 L, 187 L, 196.5 L, 212.2 L, 226.7 L, circumferential 253.9 L, 271.6 L, 286.4 L, 297.2 L, 312 L. Pitting deterioration: 154.8 bottom 2 side of pipe L. Possible infil in joint: 132.7 L, 137.9 L, 198 L, 343.3 L. | 1974 | 50
77 | TENNYSON ST | L-7 | TN-4 |  | TN-3 | 402 | 403.1 | 8 | VCP | 1% | 2023 | 10-15% | 50 | 0 | 0 | 0 | 20 | 10 | 10 | 0 | 3 | 0 | 0 | 90 | RC2 | ENCRUSTATION 61.2 L, 169.3 INFILL GUSHER M, 189.1 CRACK LONG L, ENCRUSTATION 236.8 L, SAG 312-321 M, 329-340 M. Crack 24 L, 29 L, 94 L, 110 L, 115 L, 120 L, 122 L, 150 L. Sag: 115-124 L, 128-135 L, 295-300 L. | 1974 | 50
78 | TENNYSON ST | L-7 | TN-3 |  | TN-2 | 395 | 394 | 8 | VCP | 0.52% | 2023 | 10-15% | 0 | 0 | 0 | 10 | 20 | 10 | 10 | 10 | 1 | 0 | 0 | 60 | REG2 | SAG 103-112.5 L,121.5-126.5 L, 131-140 M, 325-368 M, 380-391 L. Joint 267.6 PIECE OF PIPE ON TOP IS GONE L (no hole). Roots or debris in joints throughout/ eposits/encrustation thorugh out L, video is a little foggy/hard to tell L. Sag: 181-192 L, 231-242 L, 295-305 L. Possible crack 10 side 50 L, top of pipe 70 L, 10 side 90 L, 10 side 155 L, 10 side 180 L, 10 side 220 L, 10 side 260 w/buldge L, 10 side 306 L, 2 side 311 L, 2 side 321 L, 2 side 331 L, 2 side 361 L, Circumferential crack at tap 254 L. | 1974 | 50
79 | TENNYSON ST | L-6 | TN-2 |  | S-8 | 401 | 401.7 | 15 | VCP | 0.4% | 2023 | 10% | 20 | 0 | 10 | 0 | 20 | 10 | 10 | 0 | 2 | 0 | 0 | 70 | REG2 | 244.3’ INFILL RUNNER L in joint sealing ring deterioration L. Infil stain at joint 43 L, 52.7. Deteriorated/cracked joint w/infil stain 229.3 L, 343.7 L. Infil stain at top of pipe 2 Side: possible crack or hole 394.6 L. Deposits/encrustation throughout L. Sags: 15-47 L, 104-120 L, 156-167 L, 193-232 M, 240-253 L, 258-288 L, 312-395 M. | 1973 | 51
80 | EASEMENT | L-6 | S-8 |  | S-7 | 400 | 398.5 | 15 | VCP | 0.22% | 2023 | 10% | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | REG2 | Sags: sags throughout L except 133-182 M, 243-273 E, 292-400 (end) E | 1973 | 51
81 | EASEMENT | L-6 | S-7 |  | S-6 | 140 | 359.8 | 15 | PVC | 0.22% | 2023 | 10% | 0 | 0 | 10 | 0 | 20 | 10 | 0 | 0 | 1 | 0 | 0 | 40 | REG2 | Sag: 13-97 M, 206-360 (end) M. Some joints throughout egging/deformed L, debris/encrustation throughout L | 1973 | 51
82 | EASEMENT | L-6 | S-6 |  | S-5 | 360 | 359.5 | 15 | VCP | 0.22% | 2023 | 10% | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | REG2 | Some sagging throughout L | 1973 | 51
83 | EASEMENT | L-6 | S-5 |  | S-4 | 25 | 25.4 | 15 | VCP | 0.22% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1974 | 50
84 | RALEIGH ST | L-6 | STUB |  | R-6 | 5 | 5 | 8 | VCP | 4.44% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | RC2 | (televising didn't go to tap but it can be seen from MH) | -
85 | RALEIGH ST | L-6 | R-6 |  | R-5 | 388 | 388.6 | 8 | CIP | 4.44% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 0 | 0 | RC2 | Lined in 2023 | -
86 | RALEIGH ST | L-6 | R-5 |  | R-4 | 400 | 385.8 | 8 | VCP | 4.23% | 2023 | 5% | 0 | 0 | 10 | 10 | 0 | 10 | 10 | 10 | 15 | 10 | 0 | 50 | RC2 | Roots 360.2 L. Object wedged in the joint @ 148.3 passed with no problem, could be seal: was pushed back down. Offset joint 385 L. Circumferential crack 2.3 L, multiple circumferential cracks 362.9-366 L (from root cut saw?). Deterioration/pitting throughout L. | -
87 | RALEIGH ST | L-6 | R-4 |  | R-3 | 30 | 14.9 | 8 | DIP | 12.71% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0 | 0 | 10 | REG2 | Point repair: PVC 10.3-14.9 END. Tap has Infil coming from connection point M. Corrosion throughout pipe L | 1976 | 48
88 | RALEIGH ST | L-6 | R-3 |  | R-3A1 | 15 | 16 | 8 | DIP | - | 2023 | 5% | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 20 | REG2 | Point repair 0-3.6 w/offset L, Corrosion from 3.6 through remainder of pipe | -
89 | RALEIGH ST | L-6 | R-3A1 |  | R-3A | 90 | 94.7 | 8 | VCP | - | 2023 | 5% | 0 | 0 | 0 | 10 | 0 | 10 | 10 | 10 | 3 | 0 | 0 | 40 | REG2 | UPSTREAM; Roots 21.7 L. Longitudinal crack 52.4 L, crack in bottom of pipe 56 L, pitting/deterioration bottom ofpipe 65.5 L. Deposits/encrustation in MH R-3A & from 46-73 L. | -
90 | EASEMENT | L-6 | STR-3 |  | STR-2 | 251 | 250.8 | 8 | PVC | - | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
91 | EASEMENT | L-6 | STR-2 |  | STR-1 | 58 | 56 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
92 | EASEMENT | L-6 | STR-1 |  | R-3A | 160 | 160 | 8 | PVC | - | 2023 | 5-15% | 0 | 0 | 25 | 0 | 10 | 0 | 0 | 0 | 1 | 0 | 0 | 35 | REG2 | Offset joint 143.1 M. Egging joints throughout L. Sag 135-143.1 L, 151.7-156L. Drop into MH R-3A | -
93 | RALEIGH ST | L-6 | R-3A |  | R-2 | 100 | 101 | 8 | VCP | 13.35% | 2023 | 5% | 0 | 0 | 0 | 25 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 35 | RC2 | DEPOSITS/ENCRUSTATION THROUGHOUT PIPE, 63.5 ROOTS IN JOINT L, 67.4 ROOTS IN JOINT M, 87.3 ROOTS IN JOINT L, OUTSIDE DROP 98.9. MH R-3A has Deposits/ensrutation in the invert/narrowing L. | -
94 | EASEMENT | L-6 | R-2 |  | R-1 | 174 | 176.1 | 8 | VCP | 4.96% | 2023 | 5% | 20 | 0 | 0 | 25 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 65 | RC2 | UPSTREAM: 7.4 DEPOSITS/ENCRUSTATION M, 8.7 INFILL DRIPPER L, 30.6 ROOTS IN JOINT L, 46.6 ROOTS IN JOINT M, 71.7 ROOTS IN JOINT L, 87.3 ROOTS IN JOINT M, 97.6 ROOTS IN JOINT L, 143.9 ROOTS IN JOINT L, 162.9 ROOTS IN JOINT L, NEEDS ROOT CUT THEN LINED. Roots in joint: 61.8 L, 92.3 L, 107.3 L, 122.6 L, 127.7 L, 132.7 L. | 1976 | 48
95 | EASEMENT | L-6 | R-1 |  | Q-1 | 324 | 324.1 | 8 | DIP | 0.4% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | REG2 | Corrosion/deterioration throughout L | 1976 | 48
96 | QUITMAN ST | L-6 | Q-8 |  | Q-7 | 124 | 123.7 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | REG2 | UPSTREAM: Material change 2: PVC | -
97 | QUITMAN ST | L-6 | Q-7 |  | Q-6 | 433 | 433.7 | 8 | CIP | 4.2% | 2023 | 5-30% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17 | 0 | 0 | 10 | RC2 | Liner delamination 31.5 L, 310.3 L. | -
98 | QUITMAN ST | L-6 | Q-6 |  | Q-5 | 412 | 400 | 8 | CIP | 3.5% | 2023 | 5-50% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 10 | RC2 | Liner delamination throughout L | -
99 | QUITMAN ST | L-6 | Q-5A |  | Q-5 | 30 | 93.9 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
100 | QUITMAN ST | L-6 | Q-5 |  | Q-3 | 230 | 21 | 8 | DIP | 6.07% | 2023 | 5-10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | RC2 | Corrosion/deterioration throughout pipe L | 1976 | 48
101 | EASEMENT | L-6 | Q-3 |  | Q-2 | 65 | 225.4 | 8 | CIP | 3.3% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 3 | 0 | 0 | 10 | RC2 | Liner delamination 0 L (beginning of pipe) | 1976 | 48
102 | EASEMENT | L-6 | Q-2 |  | Q-1B | 65 | 66.5 | 8 | DIP | 75.2% | 2023 | 5-20% | 0 | 0 | 0 | 50 | 0 | 20 | 20 | 10 | 0 | 0 | 0 | 100 | REG2 | CORROSION THROUGHOUT L, Multiple fractures M and Mass of roots 52.2 E, 64.5 ENCRUSTATION M | 1976 | 48
103 | EASEMENT | L-6 | Q-1B |  | Q-1 | 20 | 19.9 | 8 | VCP | 1% | 2015 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG2 | Deposits/encrustation attached throughout L. | -
104 | EASEMENT | L-6 | Q-1 |  | Q-1A | 205 | 204.2 | 8 | DIP | 0.4% | 2023 | 5% | 20 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 40 | REG2 | Corrosion/deterioration throughout L. Possible sag 0-60 L, 138-182 L. Possible infil stains in joints: 44 L, 63.8 L, 83.9 L, 104 L, 122.4 L, 141.9 L, 158 L, 162.3 L, 182.3 L. | 1976 | 48
105 | EASEMENT | L-6 | Q-1A |  | P-1 | 130 | 127.7 | 8 | VCP | 0.4% | 2023 | 5% | 50 | 0 | 10 | 0 | 20 | 10 | 0 | 10 | 0 | 0 | 0 | 100 | REG2 | 7.5 ENCRUSTATION throughout L , 112.5 INFILL RUNNER IN JOINT M, POINT REPAIR: PVC 121.8-125 w/offset joint L. Sag 98-122 M. Pitting/deterioration 2 L, crack at to pof piep near joint 96.4 L, infil in joint at point repair RUNNER 121.8 M. | 1976 | 48
106 | PERRY ST | L-6 | P-7 |  | P-6A | 110 | 107.3 | 8 | VCP | - | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | RC2 | Point repair: PVC 57.2-60. | -
107 | PERRY ST | L-6 | P-6A |  | P-6 | 150 | 146.2 | 8 | PVC | 4.92% | 2023 | 5% | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 25 | REG2 | Egging/deformed pipe: 36 L, 61.8 L, 71.4 L, 85.5 M, 109.8 M, 123.6 L. | 1991 | 33
108 | PERRY ST | L-6 | P-6 |  | P-5 | 350 | 350.1 | 8 | CIP | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | H/RC2 | Lined in 2023 after video. | -
109 | PERRY ST | L-6 | P-5 |  | P-4 | 300 | 284.6 | 8 | PVC | 1.21% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
110 | PERRY ST | L-6 | P-4 |  | P-3 | 37 | 37.6 | 8 | DIP | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 0 | 0 | 10 | REG2 | Corrosing/deterioration throughtout pipe L. | 1976 | 48
111 | PERRY ST | L-6 | P-3 |  | P-2 | 250 | 251.7 | 8 | VCP | 5.59% | 2023 | 5-10% | 0 | 0 | 10 | 0 | 10 | 0 | 20 | 0 | 5 | 0 | 0 | 40 | H/RC2 | 1 CRACK CIRC L, 128.5 FRACTURE CIRCUMFERENTIAL L, 145.6 CRACK CIRCUMFERENTIAL L, 147.8-152.9 MULTIPLE CRACK LONGITUDINAL HINGE M , POINT REPAIR: PVC 245-249 w/offset/sag L.GOOD PIPE TO BE LINED. | 1976 | 48
112 | EASEMENT | L-6 | P-2 |  | P-1 | 75 | 75.3 | 8 | PVC | 37.81% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | 2003 | 21
113 | EASEMENT | L-6 | P-1 |  | O-1 | 224 | 225.9 | 8 | VCP | 0.4% | 2023 | 5-15% | 50 | 0 | 0 | 0 | 10 | 20 | 10 | 10 | 0 | 0 | 0 | 100 | REG2 | POINT REPAIR: PVC 0-3.8, 19.4 CRACK MULTI L, 58 ENCRUSTATION M, 84 INFILL DRIPPER/Runner M, 211.5 ENCRUSTATION, 218.6 ENCRUSTATION M. Possible infil around invert connection in MH P-1 L. Sags/high spots throughout 31-225 end L. Deterioration/pitting throughout M. Possible infil stain in joint/seperations? 38.9 L. Possible crack 2 side mid pipe L. Deposits/encrustation throughout L except: 6.3 M, 24 M, 29 M, 44.1 M, 62 M, 76.2 M, 94.9 M. | 1976 | 48
114 | OSCEOLA ST | L-6 | O-7 |  | O-6 | 350 | 349 | 8 | VCP | 4.28% | 2023 | - | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 10 | 12 | 0 | 0 | 40 | REG2 | Deposits/Encrustation 97-208 L, Deposits/encrustion in joint 74 L, 174.9 M, 270.5 L, 292 L, in joint: possible infil 282.7 M. Crack/pitting bottom 10 side 61 L, 79 L, in joint 153 L. Outside drop 343. | 1974 | 50
115 | OSCEOLA ST | L-6 | O-6 |  | O-5 | 351 | 349.1 | 8 | VCP | 4.32% | 2023 | 5% | 0 | 0 | 0 | 10 | 10 | 0 | 20 | 10 | 9 | 0 | 0 | 50 | RC2 | Roots in joint 158.3 L, 243.1 L, 253.1 L, 340.2 L. Something stuck in joint at bottom of pipe 34.1 L .Possible sag 283-320 L. Deterioration/pitting throughout L. Crack near joint 108.8 L, fracture 195.6-196.5 L, crack near joint 233 L, fracture 311.4-313.6 bottom and side of pipe L, circumferential crack 337.3 L, multiple fractures 341.6 M. | 1974 | 50
116 | OSCEOLA ST | L-6 | O-5 |  | O-4 | 402 | 401.1 | 8 | CIP | 3.48% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 1 | 0 | 0 | RC2 | UPSTREAM: Lined in 2023 after video. | 1974 | 50
117 | OSCEOLA ST | L-6 | O-4 |  | O-3A | 22 | 23.4 | 8 | VCP | 3.48% | 2023 | 5-10% | 0 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 1 | 0 | 0 | 20 | H/RC2 | UPSTREAM: Sag 0-19 M. Circumferential crack 19.7 L. | -
118 | OSCEOLA ST | L-6 | O-3C |  | O-3B | 20 | 32.9 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
119 | OSCEOLA ST | L-6 | O-3B |  | O-3A | 170 | 163.1 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG2 | UPSTREAM: Drop into MH O-3B | -
120 | OSCEOLA ST | L-6 | O-3A |  | O-3 | 190 | 189.1 | 8 | CIP | 3.48% | 2023 | 5-10% | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 2 | 1 | 0 | 20 | RC2 | Lined in 2023 after video. | -
121 | EASEMENT | L-6 | O-3 |  | O-2 | 63 | 67.5 | 8 | DIP | 44.72% | 2023 | 5% | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0 | 0 | 30 | RC2 | Corrosion throughout pipe L. Possible infil in joint 26.1 L, 43.9 L | 1974 | 50
122 | EASEMENT | L-6 | O-2 |  | O-1 | 125 | 114.7 | 8 | VCP | 5.27% | 2023 | 5% | 0 | 0 | 0 | 10 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 30 | RC2 | UPSTREAM; Roots in joints: 24.6 L, 29.5 L, 39.6 L, 59.8 L, 65.1 L, 105.4 L, 100.3 L, 110.4 L. Multiple longitudinal hinge cracks 105.4-110.4 M. LINNING WOULD DO GREAT. | 1974 | 50
123 | EASEMENT | L-6 | O-1 |  | S-4 | 424 | 426.6 | 8 | VCP | - | 2023 | 5% | 20 | 0 | 0 | 10 | 10 | 0 | 10 | 10 | 0 | 0 | 0 | 60 | H/RC2 | Roots in joint 41.7 L, 62.1 L, 68.2 L, 72.1 L, 189 L, 209.2 L,229.4 L, 234.6 L, 239.5 L, 249.6 L, 259.5 L, 274.7 L, 295 L, 299.7 L, 309.9 L, 319.8 L, 329.7 L, 339.8 L. Point repair: PVC 279-290. Something stuck in the bottom of joint 128.3: roots? Sags throughout pipe back to back L.Possible infil stain in joint 147.8 L. Crack in joint 219 L, 244.4 L, 379.8 L. Pitting/deterioration 272.4 top of pipe L. | 1974 | 50
124 | EASEMENT | L-6 | S-4 |  | S-3 | 257 | 230.5 | 15 | VCP | 0.22% | 2023 | 5-15% | 20 | 0 | 0 | 0 | 20 | 10 | 20 | 0 | 0 | 0 | 0 | 70 | REG2 | Spiral Fracture M (167.2-173.1) w/INFILL 167.2 L. Deposits/encrustation throughout L. Sag: 17-118 L, 130-213 M | 1974 | 50
125 | EASEMENT | L-6 | S-3 |  | S-2 | 300 | 300.7 | 15 | VCP | 0.22% | 2023 | 10-20% | 20 | 20 | 0 | 0 | 20 | 0 | 10 | 0 | 0 | 0 | 0 | 70 | RC2 | BROKEN PIPE AT TOP 114.4 L. Sags: 8-53 M, 81-200 M, 204-278 M. Possible infil in bottom/sides on joint 70.9 L, 77.9 L, 283.3 L. Circumferential crack 257.8 L, 294 L. | 1973 | 51
126 | EASEMENT | L-6 | S-2 |  | S-1 | 300 | 300 | 15 | VCP | 0.22% | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RC2 | NO COMMENTS | 1973 | 51
127 | LOWELL BLVD | L-6 | S-1 |  | L-2 | 311 | 310.3 | 15 | VCP | 0.22% | 2023 | 10% | 20 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 30 | REG2 | Possible infil stain at joint 63 M (none observed), Point repair: PVC 303.3. Deposits/ecrustation attached throughout pipe at the water line: grease? L | 1973 | 51
128 | NEWTON ST | L-6 | N-5 |  | N-4 | 330 | 327.3 | 8 | CIP | 2.72% | 2023 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 9 | 0 | 0 | 10 | RC2 | Lined in 2023- Sags: 185-191 L | -
129 | NEWTON ST | L-6 | N-4 |  | N-3 | 320 | 317 | 8 | CIP | 5.6% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | 9 | 0 | 0 | 20 | REG2 | .8ft delaminating of lining L, deposits/encrustation throughout pipe L | -
130 | NEWTON ST | L-6 | N-3 |  | N-2 | 300 | 291.9 | 8 | VCP | 2.68% | 2023 | 5% | 20 | 20 | 0 | 0 | 0 | 20 | 10 | 10 | 8 | 0 | 0 | 80 | REG2 | 1 Deposits/encrustation M & circumferential crack L possible infil L, circumferential crack at tap 20 L, point repair: PVC 174.9 w/offset & seperation L, 175.7 broken pipe infil/exfiltration L, 29 pitting/deterioration L, 54 pitting/deterioration L, 64.4 Cracked pipe w/possible infill L, 78 crack w/ possible infill L, spiral fracture at joint 159 M, 286.5 circumferential crack L. Deposits/encrustation throughout pipe L. | -
131 | NEWTON ST | L-6 | N-2 |  | N-1 | 300 | 303.7 | 8 | VCP | 2.2% | 2023 | 5% | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 5 | 0 | 0 | 20 | RC2 | UPSTREAM; 22ft root L. Circumferential crack 298.6 L. | -
132 | W 54TH AVE | L-6 | N-1 |  | M-1A | 164 | 162.8 | 8 | VCP | 0.4% | 2023 | 5-20% | 0 | 0 | 0 | 10 | 20 | 0 | 10 | 0 | 5 | 0 | 0 | 40 | REG2 | Sags: 17-34 L, 38-55 L, 64-90 L, 116-152 M. Roots in joint 89.8 M. Circumferential crack 159 L | 1975 | 49
133 | W 54TH AVE | L-6 | M-1A |  | M-1 | 168 | 169.9 | 8 | VCP | 0.4% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
134 | MEADE ST | L-6 | STUB |  | M-6 | 10 | 10 | 8 | VCP | 3.68% | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 |  | -
135 | MEADE ST | L-6 | M-6 |  | M-5 | 126 | 123.7 | 8 | CIP | 3.68% | 2023 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | 3 | 0 | 0 | 20 | REG2 | 0 lining delaminating, 109-112.9 lining delaminating L. Deposits/encrustation throughout L. | 1964 | 60
136 | MEADE ST | L-6 | M-5 |  | M-4 | 345 | 343 | 8 | CIP | 3.48% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 9 | 0 | 0 | 10 | REG2 | Possible infil/hole in liner towards top of pipe 216.7 L, 330.9 deposits attached encrustation L | 1964 | 60
137 | MEADE ST | L-6 | M-4 |  | M-3 | 20 | 19 | 8 | VCP | 1% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG2 | Deposits settled/compacted in MH M-4 - 5.6 into line L, deposits/encrustation throughout L, | 1964 | 60
138 | MEADE ST | L-6 | M-3 |  | M-2 | 331 | 332.1 | 8 | VCP | 3.8% | 2023 | 5% | 20 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 4 | 0 | 0 | 40 | REG2 | Offset joints: 20.7 L, 56 L, 121.8 L, 126.9 L, 162.4 L, 187.4 L, 208.1 L, 212.8 L, 217.7 L. Deposits/encrustation throughout L, Point repair: PVC 74-78.1 w/offset & seperated joint L, 106.5 crack. Possible infil in joint 5.3 (large deposits), 131.3 in bottom of joint L, 172 in bottom of joint L, 197.5 (infil stain) L, 273.1 in bottom of joint L, 303.3 in bottom of joint L, 308.2 in bottom of joint L, 318.2 in bottom of joint L. | 1964 | 60
139 | MEADE ST | L-6 | M-2 |  | M-1 | 327 | 315.4 | 8 | VCP | 3.08% | 2023 | 5% | 0 | 0 | 10 | 10 | 10 | 10 | 0 | 10 | 3 | 0 | 0 | 50 | RC2 | Point repair: PVC 2.7-7 w/offset joint L, 165.4 deposits settled compacted L, 86 root L. Root in joint 30.8 L, & 84.3 L. Joint offset 36.3 L, 41.5 L, 71.5 L, 161.9 M, 262 L, & 272.1 L. Deterioration at bottom of pipe throughout L. Sags/high spots throughout L. | 1964 | 60
140 | W 54TH AVE | L-6 | M-1 |  | L-8 | 286 | 285.1 | 8 | VCP | 1% | 2023 | 5-15% | 20 | 0 | 0 | 0 | 20 | 0 | 10 | 10 | 3 | 1 | 0 | 60 | REG2 | Infil at top of pipe 0 L (can't see where it's coming in), pitting/deterioration at joint 8.8 L, 49.4 L, 95 L, 211 L, crack at top of pipe 74.3 L, 226.8 L, crack in 2 side of pipe 100 L, crack in 10 side of pipe 130.1 L, crack in 2 side bottom 163.2L, crack 10 side 264 L, point repair: PVC 208.6-211 w/seperation at joint L. Sags throughout L except: 144-161 M, 183-192 M, 199-212 M, 253-268 M. | 1975 | 49
141 | LOWELL BLVD | L-6 | L-8 |  | CC 45A.10 (METRO) | 15 | 20.1 | 8 | PVC | - | 2023 | 5-15% | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 0 | 0 | 10 | REG2 | Sag 6.5-14 L, egging joint/tap 14.1 L | -
142 | LOWELL BLVD | L-6 | L-13 |  | L-12 | 257 | 255.5 | 8 | VCP | - | 2023 | 5-10% | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 4 | 2 | 0 | 20 | REG2 | 14.2-24.7 Deposits settled compacted M, deposits/encrustation throughout pipe L. | -
143 | LOWELL BLVD | L-6 | L-12 |  | L-11 | 331 | 56.2 | 8 | VCP | 5.77% | 2023 | 5% | 20 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 2 | 0 | 0 | 30 | REG2 | Circumfernetial crack w/infil 4 L, possible infil bottom of pipe in joint @ 8.5 L, 18.7 L, 23.8 L, 29.1 multiple fractures L, circumferential crack w/infil 30.1 L, tap 47.3 @ 10 potential infil at bottom seal L, 52.2 crack circumferential w/infil L | -
144 | LOWELL BLVD | L-6 | L-11 |  | L-10 | 56 | 321.9 | 8 | VCP | 4.7% | 2023 | 5% | 20 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 11 | 1 | 0 | 30 | REG2 | 150.7 Infiltration Weeper Joint L, 188.9 Infiltration Weeper capped tap L, Point Repair: PVC 225.2-230.5 offset L. | -
145 | W 53RD AVE | L-5 | K-3A |  | K-3 | 322 | 327.6 | 8 | PVC | - | 2023 | 5-10% | 0 | 0 | 10 | 0 | 10 | 10 | 0 | 0 | 4 | 0 | 0 | 30 | REG2 | Difficulty getting into line because of compacted deposits? Egging/deformation throught out L. 228.3ft Intruding Sealing Material Sealing Ring Loose/Poorly Fitting M, 228.8ft Survey Abandoned due to intruding gasket. UPSTREAM VIDEO; Sag 0-24 L, 106-121 L. | -
146 | KING ST | L-5 | K-3 |  | K-2 | 322 | 321.3 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
147 | KING ST | L-5 | K-2 |  | K-1 | 326 | 333.9 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
148 | W 54TH AVE | L-5 | K-1A |  | K-1 | 241.4 | 245.1 | 8 | VCP | 0.4% | 2023 | 5-10% | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 4 | 0 | 0 | 10 | RC2 | UPSTREAM; Sags 43-56 L, 120-146 L, 157-179 L, 221-238 L | -
149 | W 54TH AVE | L-5 | K-1 |  | K-6 | 130 | 131.7 | 8 | VCP | 0.4% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
150 | W 54TH AVE | L-5 | K-6 |  | K-7 | 10.4 | 12.2 | 8 | VCP | 0.4% | 2023 | 5-20% | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | REG2 | 8.9ft Sag L | -
151 | KING ST | L-5 | K-9 |  | K-8 | 339.7 | 342.7 | 8 | VCP | - | 2023 | 0% | 20 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 6 | 0 | 0 | 40 | RC2 | Roots in MH K-9 M, roots in joints throughout L, 2 Crack Circumferential L, pitting/crack 17.7 L, 61.6 roots L , pitting/crack 77.3 L, 92.3 Crack Longitudinal w/infil stain L,infil stain around joint 121 L, possible infil stain top of pipe 288.5 L, 339 Crack Circumferential L | -
152 | KING CT | L-5 | K-8 |  | K-7 | 173 | 173.1 | 8 | VCP | 4% | 2023 | 5-15% | 0 | 0 | 0 | 25 | 0 | 20 | 10 | 0 | 3 | 0 | 0 | 55 | RC2 | 4 Roots Fine Joint L, 50.2 Roots Fine Joint M, 67.9 Roots Fine Joint M, 79.5 Roots Fine Joint M, 98.9 Roots Fine Joint L, 103.6 Roots Fine Joint L, roots 108 L, 167.7 Deposits Settled Compacted M:Attempted root cut with little success, 169.7 Crack Circumferential L | 1971 | 53
153 | W 54TH AVE | L-5 | K-7 |  | L-9 | 264 | 265.5 | 8 | VCP | 0.4% | 2023 | 5-15% | 0 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 3 | 0 | 0 | 20 | REG2 | 2.7 Crack Circumferential L, multiple sags throughout L | 1971 | 53
154 | LOWELL BLVD | L-5 | L-9 |  | CC 45A.10 (METRO) | 30 | 30 | 8 | VCP | - | 2023 | 5% | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | REG2 | Point repair: PVC 22.8-27.2 w/offset joint M. Outside drop 27.2 | -
155 | KING ST | L-5 | K-5 |  | K-4 | 262 | 262.8 | 8 | VCP | 3.44% | 2023 | 0% | 0 | 0 | 0 | 25 | 0 | 20 | 0 | 0 | 7 | 0 | 0 | 45 | H/RC2 | 31.8-164.5 Deposits Attached Encrustation L-M, 169.6 Roots Fine Joint L, 189.9 Roots Fine Joint L, 204.3 Roots Fine Joint L, 219.9 Roots Fine Joint L, 224.8 Roots Medium Joint M, 240 Roots Fine Joint L, 244.9 Roots Medium Joint M, 250.7 Roots Fine Joint M, 255.1 Roots Fine Joint M. | -
156 | W 53RD AVE | L-5 | K-4 |  | J-11 | 372.7 | 380.2 | 8 | CIP | 0.4% | 2023 | 5-10% | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 2 | 0 | 0 | 10 | H/RC2 | 201.4ft Sag, Sags: 57-66L, 83-96.3 L, 166-182 L, 198-207 L, 292-304 L. Lined in 2023 after video. | -
157 | EASEMENT | L-5 | L-6C-3 |  | L-6C-2 | 60 | 79.5 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
158 | EASEMENT | L-5 | L-6C-2 |  | L-6C-1 | 213 | 211.5 | 8 | PVC | - | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
159 | W 55TH AVE | L-5 | L-6D |  | L-6C-1 | 26 | 95.1 | 8 | VCP | 2.28% | 2023 | 5-15% | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 20 | REG2 | UPSTREAM; Point repair: PVC 0-3,sag/belly 0-28 M, sag 32-80 L | -
160 | W 55TH AVE | L-5 | L-6C-1 |  | L-6C | 293 | 292.8 | 8 | VCP | 0.4% | 2023 | 5-15% | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 10 | 6 | 0 | 0 | 30 | REG2 | Point Repair: PVC 0-3.9, high spot 0-5.5 L, sag 8.6-25.8 L, buldge in side of pipe 9 oclock side L, sag 82-97 L, sag 123-132 L, 105.8 root L, 111 root L, roots in joint 116.4 L, 174-188 Sag L, roots in joint 181.8 L, sagging 217-264 L. | -
161 | W 55TH AVE | L-5 | L-6C |  | L-6B-1 | 98 | 97.3 | 8 | VCP | 0.4% | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG2 | Sag 7-14 L, 22ft-32 Sag L, sag 49-62 L, sag 75-88 L, Point Repair: PVC 93.5-97.3 w/offset joints L | -
162 | W 55TH AVE | L-5 | L-6B-3 |  | L-6B-2 | 75 | 78.3 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
163 | EASEMENT | L-5 | L-6B-2 |  | L-6B-1 | 200 | 212.2 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
164 | W 55TH AVE | L-5 | L-6B-1 |  | L-6B | 135.6 | 137.3 | 8 | VCP | - | 2023 | 5-15% | 0 | 0 | 0 | 10 | 10 | 10 | 10 | 10 | 3 | 0 | 0 | 50 | RC2 | Point Repair: PVC 0-4.7, joint missing pieces 4.1 L, roots in joint 5.4 L, sag 11-21 L, sag 39-46L, sag 71-87 M, 101-133 L, 127.3 Fracture Spiral L. Debris/encrustation throughout L. | -
165 | W 55TH AVE | L-5 | L-6B |  | L-6A | 103 | 102.4 | 8 | VCP | 0.4% | 2023 | 5% | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 2 | 0 | 0 | 20 | REG2 | Roots in joint 0.1 L, 13.1ft root L, 93.8 ft. Crack Circumferential L | -
166 | LOWELL BLVD | L-5 | L-6A |  | CC 45A.8 (METRO) | 50 | 32.3 | 8 | VCP | 0.8% | 2023 | 15% | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG2 | UPSTREAM; Point Repair: PVC 0-5.5ft, possible infil in bottom/side of pipe 9.5 L, | 1978 | 46
167 | LOWELL BLVD | L-6 | CC 45A.8 (METRO) |  | L-6 | 50 | 14.5 | 12 | PVC | 0.8% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | 1978 | 46
168 | LOWELL BLVD | L-6 | L-6 |  | L-5A1 | 266 | 265.1 | 8 | VCP | 5.76% | 2023 | 10% | 20 | 0 | 10 | 0 | 0 | 0 | 20 | 0 | 3 | 0 | 0 | 50 | REG2 | Point Repair: PVC 0-8.3, possible infil bottom/side of pipe joint 72.3 L, 77.5 L, 87.2 L,107.6 L, 138.1 L, 147.5 L, 173.3 L, 245.1 L, 131.6 Crack Circumferential L, Point Repair: PVC 147.5-151.3 Joints Offset L, 200.7 Crack Circumferential L, 205.2 Crack Circumferential L, 224.9 Crack Longitudinal L, Point Repair: PVC 240.2-245.2 Joints Offset M, 257.8 Crack Multiple M | 1978 | 46
169 | LOWELL BLVD | L-6 | LH-3 |  | LH-2 | 95 | 94 | 8 | PVC | 2% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | 2007 | 17
170 | LOWELL BLVD | L-6 | LH-2 |  | LH-1 | 110 | 110.5 | 8 | PVC | 6.81% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | 2007 | 17
171 | LOWELL BLVD | L-6 | LH-1 |  | L-5A1 | 25 | 20.9 | 8 | PVC | 6.95% | 2023 | 5% | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | REG2 | UPSTREAM; Infiltration in MH LH-1 18.3 in invert connection: runner M | 2007 | 17
172 | LOWELL BLVD | L-6 | L-5A1 |  | L-5 | 132 | 130.9 | 8 | VCP | 5.76% | 2023 | 10-15% | 0 | 0 | 0 | 0 | 20 | 0 | 10 | 0 | 0 | 0 | 0 | 30 | REG2 | 1.2 ft. Circumferential fracture L. Sags 0-21 M, 38-91 L, 107-206 L, 209-232 M. | 1978 | 46
173 | LOWELL BLVD | L-6 | L-5 |  | L-4 | 182 | 105.3 | 8 | CIP | - | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
174 | LOWELL BLVD | L-6 | L-4 |  | L-3 | 182 | 44.3 | 8 | PVC | - | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
175 | EASEMENT | L-6 | L-3 |  | L-2 | 6 | 37.3 | 8 | PVC | - | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
176 | JULIAN ST | L-5 | J-12 |  | J-11 | 193 | 287.5 | 8 | PVC | 7.3% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
177 | W 53RD AVE | L-5 | J-11 |  | J-10 | 12 | 10.9 | 8 | VCP | 7.3% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RC3 | NO COMMENTS | -
178 | W 53RD AVE | L-5 | J-10 |  | J-9 | 47.4 | 47.4 | 8 | VCP | 4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RC3 | NO COMMENTS | -
179 | JULIAN ST | L-5 | J-9 |  | J-8 | 176 | 174.8 | 8 | VCP | 3.8% | 2021 | - | 0 | 0 | 25 | 0 | 0 | 10 | 0 | 0 | 4 | 3 | 0 | 35 | REG3 | Deposits/encrustation attached thorughout L, offset/broken joint @ 157.2 M | -
180 | W 53RD PL | L-5 | J-8A |  | J-8 | 247 | 245.2 | 8 | VCP | 0.4% | 2018 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
181 | JULIAN ST | L-5 | J-8 |  | J-7 | 154 | 153.3 | 8 | VCP | 3.8% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 2 | 0 | 0 | REG3 | NO COMMENTS | -
182 | JULIAN ST | L-5 | J-7 |  | J-6 | 325 | 81.4 | 8 | VCP | 3.8% | 2017 | - | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 10 | 1 | 2 | 0 | 30 | RC3 | UPSTREAM; Break or hole in bottom of pipe joint 2.1 L. Deterioration/pitting & debris throughout L. ABANDONED: INTRUDING TAP 81.4, DIDN'T GO DOWNSTREAM. | -
183 | W 53RD AVE | L-5 | STUB:I-3A |  | I-3 | 122.5 | 124.8 | 8 | VCP | - | 2023 | 5% | 20 | 0 | 0 | 10 | 10 | 10 | 20 | 20 | 4 | 1 | 0 | 90 | H/RC3 | 3 Roots Fine Joint L , 27.6 Crack Longitudinal L, 68.6 Crack Longitudinal L, sag 78.5-85 L, 88.4 Crack Longitudinal L w/infil stain L, longitudinal crack in the bottom of pipe 105.7-109 L, sags 108-115, 122-129 L, 131.2 Crack Multiple L, 191.6 Crack Circumferential L, 200.4 Crack Circumferential L, 201.9 Crack Longitudinal L, 203.2-214.4 multiple Cracks M, 214.4 Roots . Debris/encrustation throughout L, pitting/deterioration throughout L-M. | -
184 | W 53RD AVE | L-5 | STUB:I-3B |  | I-3 | 212.9 | 214.4 | 8 | VCP | - | 2023 | 5% | 0 | 0 | 0 | 10 | 10 | 10 | 10 | 10 | 3 | 0 | 0 | 50 | REG3 | 0.3 Crack Circumferential w/roots L, 9.2 roots L, 17.3 Deposits Attached Encrustation/joint deterioiration L , 82.9 roots L. Sag 113.9-123.8 L. Deposits/encrustation throughout L, pitting/deterioration throughout L. Not a proper cap at the end of the pipe/bricks. | -
185 | IRVING ST | L-5 | I-3 |  | I-2 | 325.1 | 326.1 | 8 | CIP | - | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 0 | 0 | REG3 | Lined in 2023 after video. | -
186 | IRVING ST | L-5 | I-2 |  | I-1 | 330.5 | 330.2 | 8 | VCP | - | 2023 | 5% | 0 | 20 | 0 | 10 | 0 | 0 | 10 | 10 | 7 | 3 | 0 | 50 | RC3 | Point repair: PVC 0-12, 12.7 Crack Multiple L, 12.8 Roots Fine Joint L, 24.9 pitting in the bottom of pipe L, 25.6-30. Crack Longitudinal w/pitting/missing pieces M, 44.2 Crack Spiral L, 46.848 cracked/Broken Pipe Soil Visible M, pitting/piece missing 85.6, 122.7 138.5, 175, 183.9 L, crack in joint @ 172 L, 277.7 root L, 287.7 Roots Fine Joint L, 320.5 alignment: Right, 329.4 Crack Spiral L | -
187 | W 54TH AVE | L-5 | I-1A |  | I-1 | 351.6 | 351.2 | 8 | PVC | 0.4% | 2023 | 5-10% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 3 | 1 | 0 | 20 | REG3 | UPSTREAM; Joints throughout possibly egged L. Sags throughout L. | -
188 | W 54TH AVE | L-5 | I-1 |  | J-6A | 206.7 | 207.4 | 8 | VCP | 1% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
189 | W 54TH AVE | L-5 | J-6A |  | J-6 | 236.5 | 236 | 8 | VCP | - | 2023 | 5% | 0 | 0 | 25 | 0 | 10 | 10 | 10 | 0 | 4 | 5 | 0 | 55 | H/RC3 | Sags 10.8-21.8L, 35.6-56 L, 143.4-177 L. Point repair:PVC offset 89.3-92.7 Joint Separated M, 183.9 Crack Longitudinal L, point repair: PVC 227.1-231.7 offset L seperated/broken joint 231.7 M. Deposits/ecrustation throughout L. | -
190 | JULIAN ST | L-5 | J-6 |  | J-5 | 399 | 385.6 | 8 | VCP | 2.94% | 2013 | - | 20 | 0 | 0 | 0 | 0 | 20 | 10 | 10 | 7 | 7 | 0 | 60 | RC3 | Spiral fracture 6.8 L, Point repair: PVC 9.4-13.1. Joint seperation at point repair 13.1 L with infil L, crack near joint/top 15.1 L, circumferential crack near joint 42.9 L, circumferential crack near joint 50.6 L, multiple fracture near joint 54.6 L, longitudinal fracture 63.7 L, circumferential fracture 81.9 L, circumferential crack near top of joint 125.9 L, longitudinal crack near top of pipe/joint 131.3 L, circumferential crack near joint top of pipe 149.1 L, offset joint 161.1 L. Deterioration/pitting throughout L, deposits attached throughout L except: 50.7 M, 105.2 M, 164 M, 189.9 M. Roots in joints thorughout L. ABANDONED: couldn't pass deposits at 189.9. UPSTREAM; Drop into MH J-5. Crack near joint top of pipe 13.8 L, point repair: PVC 18.9-21.7, encrustaiton/deposits attached 44.7 L, 157.0 M, 189.9 M, 195.7 M. ABANDONED; couldn't pass deposits. Sags throughout L. | -
191 | JULIAN ST | L-5 | J-5 |  | J-4 | 26 | 26.1 | 8 | DIP | 2.28% | 2013 | - | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 0 | 0 | 0 | 30 | REG3 | Deterioration throughout M. Possible circumferential crack 14.1 L. | 1976 | 48
192 | W 55TH AVE | L-5 | STUB |  | J-4C | 6 | 6.2 | 8 | VCP | - | 2014 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
193 | W 55TH AVE | L-5 | J-4C |  | J-4B | 322 | 322 | 8 | PVC | 0.4% | 2013 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 7 | 0 | 0 | 10 | RC3 | Sags through out L. | -
194 | W 55TH AVE | L-5 | J-4B |  | J-4A | 400 | 436.6 | 8 | PVC | 0.4% | 2013 | - | 0 | 0 | 25 | 0 | 20 | 0 | 0 | 0 | 14 | 0 | 0 | 45 | REG3 | Sags thorughout L. Offset joint: 211.9 M, 215.1 M. ABANDONED DUE TO OFFSET 215.1. UPSTREAM; Sags: 101-161 M, 184-218 L. ABANDONED DUE TO OFFSET 218. | -
195 | W 55TH AVE | L-5 | J-4A |  | J-4 | 83 | 81.6 | 8 | DIP | 0.94% | 2013 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | UPSTREAM; Point repair: PVC 0-17. Point repair: PVC 66-80. | -
196 | JULIAN ST | L-5 | J-4 |  | J-3 | 164 | 162 | 8 | VCP | 1.48% | 2017 | - | 20 | 0 | 0 | 10 | 10 | 10 | 10 | 10 | 2 | 0 | 0 | 70 | RC3 | Roots in joint: 56.6 L, 61.6 L, 66.3 L, 139.3 L. Sags: 15-23 L, 80-87 L. Deterioration/pitting & debris throughout L. Crack near joint 119.8 L, fracture at joint 134.8 L, circumferential crack 157.5 L. Possible Infil in joint 149.3 L. | 1976 | 48
197 | JULIAN ST | L-5 | J-3 |  | J-2 | 28 | 27.1 | 8 | VCP | 1.8% | 2013 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1976 | 48
198 | JULIAN ST | L-5 | J-2 |  | J-1 | 212 | 209.1 | 8 | VCP | 4% | 2017 | - | 20 | 0 | 0 | 0 | 10 | 0 | 10 | 20 | 3 | 0 | 0 | 60 | REG3 | UPSTREAM; Circumferential fracture 1.5 L, multiple circumferential cracks 7.1 L (root cut saw), deterioration 110.5-124.1 M, circumferential crack 205.3 L. Sag: 65-72 L. Point repair: PVC 128.7-133.1. Possible infil in bottom of joint: 39.6 L, 54.1 L, 59.4 L, 89.0 L, 152.2 L, 181.8 L, 201.0 L. | 1978 | 46
199 | W 55TH PL | L-5 | J-1B |  | J-1A | 250 | 250.7 | 8 | PVC | 1.96% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
200 | W 55TH PL | L-5 | J-1A |  | J-1 | 213.8 | 213.8 | 8 | PVC | 0.465% | 2021 | - | 20 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 40 | REG3 | Possible infil inside MH J-1A next to invert L. Possible sags @ 31-38 L, 62-78 L, 84-95 L, 129-140 L, 181-212 end M. Possible egging thorughout: joints L. | -
201 | W 55TH PL | L-5 | J-1 |  | L-5B | 415 | 415.6 | 8 | PVC | 0.89% | 2021 | - | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 10 | 5 | 0 | 0 | 30 | REG3 | Offset joint @ approx. 2.5 L, possible sag at approx. 67-72 L, 138-150 L, & 185-195 L. Joints @ approx. 181 L, 254 L, 266 L, 289 L, 326 L, & 399 L looks like they might be egged, end MH connection was clay & looks like it might be offset/broken. | 1978 | 46
202 | W 55TH PL | L-5 | L-5B |  | L-5A | 223 | 223.9 | 8 | CIP | 7.43% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | Lined in 2023 | 1978 | 46
203 | W 55TH PL | L-5 | L-5A |  | L-5 | 245 | 248.3 | 8 | VCP | 0.4% | 2023 | 5-15% | 20 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 30 | REG3 | 1.2 Circumferential crack L. Circumferential crack 32.2 L, 126.2 spiral crack L. Possible infil in bottom of joint 55, 65, 70, 75, 95, 105 L. | 1978 | 46
204 | W 53RD AVE | L-5 | G-6D-3 |  | G-6D-2 | 154.5 | 151.3 | 8 | PVC | 6.14% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2021 | 3
205 | W 53RD AVE | L-5 | G-6D-2 |  | G-6D-1 | 64.1 | 60.2 | 8 | PVC | 5.04% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2021 | 3
206 | W 53RD AVE | L-5 | G-6D-1 |  | G-6D | 60.8 | 54.7 | 8 | PVC | 0.57% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2021 | 3
207 | W 53RD AVE | L-5 | G-6D |  | G-6C | 25 | 23.4 | 8 | VCP | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
208 | REGIS RD | L-5 | G-6C2 |  | G-6C1 | 143 | 141.7 | 8 | PVC | 1% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1988 | 36
209 | REGIS RD | L-5 | G-6C1 |  | G-6C | 237.7 | 237.7 | 8 | PVC | 2% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1988 | 36
210 | W 53RD AVE | L-5 | G-6C |  | G-6B | 134 | 135 | 8 | VCP | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
211 | W 53RD AVE | L-5 | G-6B |  | G-6A | 164 | 164.6 | 8 | VCP | - | 2021 | - | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 3 | 3 | 0 | 20 | RC3 | Roots in joint @ 18 L, 75 L, 82 L, 91 L, 103 L, 115 L, 127 L, 133 L, 142 L, 151 L. Roots in tap @71.6 M. Multiple fracture @ 82.0 L, circumferential crack @ 130.0 L, crack @ 153.9 L. Possible candidate for lining | -
212 | W 53RD AVE | L-5 | G-6A |  | G-6 | 223 | 221.2 | 8 | VCP | - | 2021 | - | 0 | 0 | 25 | 10 | 0 | 0 | 10 | 0 | 3 | 0 | 0 | 45 | RC3 | Offset joint @ 81.6 M, point repair from 196.1 - 197.4, defective point repair @ 221.2 couldn't pass M. Material change @ 221.2 to PVC to the MH, outside drop.Roots in joint @ 5 L, 8 L. Crack at joint @ 11 L. NO UPSTREAM VIDEO/CAN SEE THE END. Survey abandoned @ 221.2. | -
213 | GROVE ST | L-5 | G-8 |  | G-7 | 235 | 235.5 | 8 | PVC | - | 2021 | - | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 10 | 5 | 0 | 0 | 30 | REG3 | Calcium build up at the start of pipe L, point repair (metal?) @ 138.4 -140.2, pipe out of round & possible break @182.9 L | -
214 | GROVE ST | L-5 | G-7 |  | G-6 | 175 | 192.2 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 20 | REG3 | Possible egging: joint @ 45 L, 58 L, 85 L, 97 L, 111 L, 125 L, 143 L, 164 L, 190 L. Sag @ 190-192 end L. Outside drop @ 192.2 | -
215 | W 53RD AVE | L-5 | G6-1 |  | G-6 | 346.1 | 346.1 | 8 | VCP | - | 2021 | - | 0 | 0 | 10 | 10 | 0 | 10 | 10 | 10 | 11 | 5 | 0 | 50 | REG3 | Roots in joint @ 1 L, 39 L, 90 L, 96 L, 115 L, 208 L, 211 L, 220 L. Deterioration/pitting throughout L. Some cracks at the top of the pipe @ begining L, multiple fractures @ 39.1 L, longitudinal fracture @ 42.5 L & 45.4 L, roots in possible tap @ 77.2', circumferential fractures @ 96.2 L, 133.0 L, 169.4 L & 312.5 L, multiple fractures @208.9 L, fine roots on the top and side of tap @ 217.8 L, circuferentail fracture @ 218.5 L, longitudinal fracture @ 224.1 L, 227.4 L, 248.3 L & 282.4L , calcium deposit attached @ 312.5, point reair starting @ 332.0 - 334.9 offset L, material change to PVC @ 341.9 offset L. Outside drop @ 346.1. Possible candidate for lining. | -
216 | GROVE ST | L-5 | G-6 |  | G-5 | 325.6 | 325.6 | 8 | PVC | - | 2021 | - | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 6 | 0 | 0 | 20 | REG3 | Furnco at start of pipe, offset joint @ approx. 1.0 L. Egging: joint @ 60 L, 193 L, 206 L, 245 L, 272 L, 284 L, 309 L. | -
217 | GROVE ST | L-5 | G-5 |  | G-4 | 327 | 328.9 | 8 | PVC | - | 2021 | - | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 10 | 5 | 0 | 0 | 30 | REG3 | Intruding sealing ring on bottom of pipe @ 3.0 L, sag @ 198-224 L, 273-289 L, 297-302 L. Egging: joint @ 54 L, 57 L, 66 L, 79 L, 145 L, 172 L, 275 L. | -
218 | W 54TH AVE | L-5 | STUB |  | G-4 | 249 | 252.6 | 8 | VCP | - | 2014 | - | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 10 | 3 | 1 | 0 | 30 | RC3 | UPSTREAM; Drop into MH G-4. Deterioraton/pitting throughout L. Hole in top of pipe where rock was pushed in 198.3 L. Cap at end is just brick. | -
219 | GROVE ST | L-5 | G-4 |  | G-3 | 412 | 414.4 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 10 | 10 | 20 | 0 | 10 | 7 | 0 | 0 | 50 | REG3 | Fine roots in tap @ 80.1 M, deposits attached @ 245.1 M & 285.2 M calcium. Sag @ 178-190 L, 370-385 L. Egging: Joint @ 141 L, 179 L, 192 L, 280 L, 398 L, | -
220 | W 54TH AVE | L-5 | G-3H |  | G-3G | 52 | 51.6 | 8 | PVC | 0.4% | 2018 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | NO COMMENTS | 1983 | 41
221 | W 54TH AVE | L-5 | G-3G |  | G-3F | 149 | 148.5 | 8 | PVC | 0.4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1983 | 41
222 | W 54TH AVE | L-5 | G-3F |  | G-3E | 28 | 24.4 | 8 | PVC | 0.4% | 2021 | - | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 10 | 0 | 0 | 0 | 30 | REG3 | Sag from 15-24 w/possible egging L. Grit in line L. Looks ok | 1983 | 41
223 | EASEMENT | L-5 | G-3E |  | G-3D | 111 | 110.3 | 8 | VCP | 3.24% | 2021 | - | 0 | 0 | 10 | 0 | 10 | 10 | 0 | 0 | 1 | 0 | 0 | 30 | REG3 | Sag from 104-108 L: offset joint L. Deposits/encrustation: Calcium throughout L. | 1977 | 47
224 | EASEMENT | L-5 | G-3D |  | G-3C | 73 | 72.1 | 8 | VCP | 2.2% | 2017 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG3 | Deposits/encrustation attached throughout L. | 1977 | 47
225 | EASEMENT | L-5 | G-3C |  | G-3B | 285 | 287.7 | 8 | VCP | 2.16% | 2021 | - | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 4 | 0 | 0 | 20 | REG3 | UPSTREAM// Possible sag @ 34-44 L, 86-99 L, 107-121 L. Deposits/encrustation: calcium throughout L. | 1977 | 47
226 | W 55TH AVE | L-5 | G-3B |  | G-3 | 328 | 330.4 | 8 | VCP | 0.4% | 2021 | - | 0 | 0 | 25 | 0 | 10 | 0 | 0 | 0 | 3 | 0 | 0 | 35 | REG3 | Light sagging throughout @ 41-67 L, 91-127 L, 155-211 L, 222-233 L, 245-256 L, 260-270 L, 288-301 L, 331-327 L. Material change: PVC @ 327 offset M. Outside Drop before MH @ 330.3. May be a good candidate for lining. | 1977 | 47
227 | W 55TH AVE | L-5 | STUB |  | G-3A | 10 | 10 | 8 | VCP | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 |  | -
228 | W 55TH AVE | L-5 | G-3A |  | G-3 | 149 | 148.4 | 8 | VCP | 0.4% | 2019 | - | 0 | 0 | 10 | 0 | 10 | 0 | 10 | 20 | 1 | 0 | 0 | 50 | RC3 | Circumferential crack 3.3 L, sag 32-43 L, sag 97-107 L, deterioration 130-148 M, off set joint 148 L. Drop in MH G-3 | -
229 | GROVE ST | L-5 | G-3 |  | G-2 | 408 | 412.2 | 8 | PVC | - | 2021 | - | 20 | 0 | 0 | 0 | 10 | 20 | 0 | 0 | 7 | 0 | 0 | 50 | REG3 | Calcium deposits attached at joints @ 60.2 M w/infil: runner L & 65.8 L, 79.3 L. Egging: joint @ 75 (tap) L, 79 L, 105 L, 136 (tap) L, 160 L, 174 L, 187 L, 259 L, 334 (tap) L, 335 L, 348 L, 376 L, 392 L, end 414 L. Possible sag @ 46-66 L, 119-133 L, 145-160 L, 166-177 L, 200-221 L, 236-245, 252-262 L, 317-334 L, 334-349 L, 370-376 L, 390- 414 end L. Footage is wrong, several spots where the counter wasn't keeping up with the camera moving. | -
230 | W 55TH PL | L-5 | STUB |  | G-2B | 10 | 10 | 8 | VCP | 0.4% | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
231 | W 55TH PL | L-5 | G-2B |  | G-2A1 | 134 | 131.5 | 8 | VCP | 0.4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
232 | W 55TH PL | L-5 | G-2A1 |  | G-2A | 162 | 162.6 | 8 | VCP | 0.4% | 2021 | - | 20 | 0 | 10 | 10 | 10 | 0 | 0 | 0 | 2 | 0 | 0 | 50 | REG3 | Point repair: PVC 134.8- 137. Possible sag @ approx. 9-18 L, 20-38 L, 76-84 L, 118-160 L. Roots in joint @ 33 L. Sealing ring failing/intruding M: 63.4 w/infil: dripper L, 68.6 L, 74.1 L, & 99.3 L. | -
233 | W 55TH PL | L-5 | G-2A |  | G-2 | 56 | 56.2 | 8 | VCP | - | 2021 | - | 0 | 0 | 10 | 0 | 10 | 20 | 0 | 0 | 0 | 0 | 0 | 40 | REG3 | Point repair: PVC @ 30.6-32.3. Possible sag @ 48-56 end L. A lot of grit in line M (before cleaning). Inside drop @ 56.2 offset L W/NO ACCESS FROM TOP | -
234 | W 55TH PL | L-5 | G-2 |  | G-1 | 15 | 14.8 | 8 | PVC | 0.4% | 2013 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1977 | 47
235 | W 55TH PL | L-5 | G-1 |  | L-4H | 347 | 346.1 | 8 | VCP | 3.52% | 2021 | - | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 2 | 0 | 0 | 20 | RC3 | Circumferential fracture @ 343.1 w/roots L. Roots in joint @ 194 L, 205 L, 210 L, 215 L, 232 L, 237 L, 248 L, 264 L, 269 L, 296 L, 302 L. Possible candidate for lining. | 1977 | 47
236 | W 55TH PL | L-5 | J-1B |  | L-4H | 246 | 247.4 | 8 | PVC | 2.22% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 3 | 0 | 0 | 10 | REG3 | Material change to steel @ 237.1. Egging: joint @ 71 L, 80.5 (tap) L, 129 L, 208 L. Inside drop @ 246.0. | -
237 | EASEMENT | L-5 | L-4H |  | L-4I | 140 | 140.6 | 8 | VCP | 1.56% | 2023 | 5% | 0 | 0 | 0 | 0 | 20 | 10 | 10 | 0 | 0 | 0 | 0 | 40 | H1 | UPSTREAM; Point repair: PVC 0-6.3ft, 128.7ft Crack Circumferential L. Possible sag 0-15 M, 32-43 L, 69-80 M. Deposits/encrustation throughout pipe L. | -
238 | EASEMENT | L-5 | STUB |  | L-4L | 10 | 10 | 8 | PVC | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 |  | -
239 | EASEMENT | L-5 | L-4L |  | L-4K | 184 | 184.8 | 8 | PVC | - | 2019 | - | 0 | 0 | 0 | 0 | 20 | 10 | 0 | 0 | 0 | 0 | 0 | 30 | REG3 | Encrustation/deposits attached: grease throughout pipe L. Deposits/encrustation at joint 39.5 & 52.0 possible infiltration L. Sags: 26-45 M, 77-82 L, 113-125 L, 133-148 L, 164-181 M. | -
240 | EASEMENT | L-5 | L-4K |  | L-4J | 10 | 7.6 | 8 | PVC | - | 2019 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG3 | Deposits/encrustation attached throughout (grease) L. | -
241 | EASEMENT | L-5 | L-4J |  | L-4I | 331 | 328.6 | 8 | PVC | - | 2020 | - | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 1 | 0 | 0 | 20 | H1 | UPSTREAM; Sag: 124-139 L, 175-187 L. Deposits/encrustation throughout (grease) L. | -
242 | EASEMENT | L-5 | L-4I |  | L-4G | 161 | 162.6 | 8 | VCP | 1.56% | 2021 | - | 0 | 0 | 25 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 35 | REG3 | PVC to approx. 5.3/material change to VCP, possible joint sepperation? M, circumferential fracture (multiple) @ approx. 160 L. Good canidate for lining | -
243 | EASEMENT | L-5 | L-4G |  | L-4F | 351 | 346.7 | 8 | VCP | 4.54% | 2020 | - | 20 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 1 | 0 | 0 | 40 | H/RC3 | UPSTREAM; General Observation (bubbling seal?) 72.7 L. Infiltration in bottom of joints: 18.1 L, 23.8 L, 116.3 L, 121.5 L, 137.6 L, 148.2 L, 185.8 L, 223.1 L, 250.1 L, 266.3 L, 276.7 L, 282.2 L, 298.2 L, 303.6 L, 335.7 L. Deposits/encrustation throughout L. | 1977 | 47
244 | EASEMENT | L-5 | L-4F1 |  | L-4F | 159 | 158.2 | 8 | VCP | 4.52% | 2019 | - | 50 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 70 | REG3 | Multiple circumferential crack 7.2 L (root cut saw), looks like multiple circumferential cracks w/encrustation or possible infil 40.3-46.0 L, circumferential crack w/infil runner 156.2 M | 1977 | 47
245 | EASEMENT | L-5 | L-4F |  | L-4E | 215 | 347.4 | 8 | VCP | 0.4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 1 | 0 | 0 | 10 | H1 | UPSTREAM// Deposits/encrustation throughout | 1977 | 47
246 | EASEMENT | L-5 | L-4E |  | L-4D | 169 | 212.6 | 8 | VCP | 0.4% | 2023 | 10% | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | RC3 | UPSTREAM: ¼ FULL THROUGH OUT – 69’ CAM UNDER WATER BECAUSE OF SAG | 1977 | 47
247 | EASEMENT | L-5 | L-4D |  | L-4C | 307 | 307 | 8 | VCP | 0.4% | 2023 | 10-50% | 0 | 0 | 25 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | REG3 | UPSTREAM: 4 JOINT OFFSET M, SAG 20.5-30 M, SAG 263-END: 279.6’ CAM UNDER WATER M | 1977 | 47
248 | EASEMENT | L-5 | L-4C |  | L-4B | 298 | 297.4 | 8 | VCP | 0.4% | 2023 | 5-30% | 0 | 0 | 0 | 0 | 20 | 10 | 20 | 0 | 0 | 0 | 0 | 50 | H/RC3 | 2 CRACK M, 207.6-212 FRACTURE MULTI M. Deposits/encrustation throughout pipe L. Sags: 6-122 M, 200-208 M, 258-295 M. | 1977 | 47
249 | EASEMENT | L-5 | L-4B |  | L-4A | 268 | 268.2 | 8 | VCP | 0.4% | 2023 | 10-30% | 0 | 0 | 0 | 0 | 20 | 0 | 10 | 0 | 0 | 0 | 0 | 30 | H1 | Sags: 20-47 M, 52-64 M, 80-123 M, 130-213 M, 218-268 END M. Circurferential crack: 38.3 L, 51.4 L, 60.8 L, 66.2 L, 71.9 L, 87.9 L, 93.5 L, 109.6 L, 120.3 L, 147 L, 168.2 L, 173.3 L, 216.8 L ALL LOOK LIKE THEY'RE FROM ROOT CUT SAW. | 1977 | 47
250 | EASEMENT | L-5 | L-4A |  | L-2 | 250 | 251.1 | 8 | CIP | 0.4% | 2020 | - | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 20 | 0 | 0 | 0 | 60 | REG3 | Sag: 16.5-35 M, 50-62 L, 102-194 M-E, 202-221 M. Damage to liner 241.8-247.8 L, delamination 247.8-250.6 M | 1977 | 47
251 | EASEMENT | L-5 | BE-57A |  | BE-57 | 210 | 213.3 | 10 | P.E. | 0.2% | 2021 | - | 0 | 20 | 0 | 0 | 40 | 20 | 0 | 0 | 2 | 0 | 0 | 80 | H1 | Sags throughout starting @ approx. 89-130, 132-150, & 185-213 5%-50%+ E. Deposits/encrustation throughout: grease, grease glob at top of pipe approx 138.8 M. Looks like hole/break through at approx. 189.7 (blue rag?) 2 side L. | -
252 | EASEMENT | L-4 | BE-57 |  | BE-56 | 261 | 264.7 | 10 | P.E. | 0.2% | 2019 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | REG3 | Gauges throughout line. Tap in MH BE-56 | -
253 | EASEMENT | L-4 | BE-56 |  | BE-56A | 102.65 | 102.65 | 10 | P.E. | 0.23% | NEW | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 2 | 0 | 0 | 10 | REG3 | NEW ALIGNMENT; Sag: 11-19 L, 25-47 L, 75-90 L, 97-111 L. | -
254 | EASEMENT | L-4 | BE-56A |  | BE-56B | 166.67 | 166.67 | 8 | PVC | 0.11% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NEW LINE | -
255 | EASEMENT | L-4 | BE-56B |  | BE-56C | 152 | 152.29 | 8 | PVC | 0.14% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NEW LINE | -
256 | EASEMENT | L-4 | BE-56C |  | BE-55 | 260.66 | 260.66 | 10 | P.E. | 0.23% | NEW | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 2 | 0 | 0 | 10 | REG3 | NEW ALIGNMENT; Sags throughout L. | -
257 | W 56TH AVE | L-4 | BE-55 |  | DM-1 | 21 | 19.5 | 10 | P.E. | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
258 | EASEMENT | L-4 | DM-9 |  | DM-8 | 133 | 132.3 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
259 | EASEMENT | L-4 | DM-8 |  | DM-7 | 56 | 54.6 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
260 | EASEMENT | L-4 | ELM-1 |  | ELM-2 | 255 | 258.9 | 8 | PVC | 2.35% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2002 | 22
261 | EASEMENT | L-4 | ELM-2 |  | DM-7 | 160 | 160.5 | 8 | PVC | 4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2002 | 22
262 | EASEMENT | L-4 | DM-7 |  | DM-6 | 330 | 329.1 | 8 | PVC | - | 2023 | 5% | 20 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 30 | H/RC3 | Some egging/out of round joints throughout L, 328.9ft DM-7 buried, Infiltration runner in DM-7 L at the invert connection | -
263 | W 55TH AVE | L-4 | DM-6 |  | DM-5 | 250 | 251.6 | 8 | PVC | 0.49% | 2021 | - | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 10 | 5 | 0 | 0 | 30 | REG3 | Joints look egged @ 35 L, 72 L, 85 L. Egged pipe @ approx. 145-158, 201 L (tap). Sag @ 21-41 L, 66-85 M, 138-152 M. | 1983 | 41
264 | W 55TH AVE | L-4 | DM-5B |  | DM-5A | 269 | 270.5 | 8 | PVC | 1.66% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1983 | 41
265 | W 55TH AVE | L-4 | DM-5A |  | DM-5 | 271 | 270.4 | 8 | PVC | 1.89% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1983 | 41
266 | EASEMENT | L-4 | DM-5 |  | DM-4 | 201 | 202 | 8 | PVC | 3.09% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1983 | 41
267 | EASEMENT | L-4 | DM-4 |  | DM-3 | 56 | 56 | 8 | PVC | 0.54% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1983 | 41
268 | EASEMENT | L-4 | DM-3 |  | DM-2 | 290 | 294.4 | 8 | PVC | 0.44% | 2021 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | REG3 | Sag @ approx. 146-157 L, 213-223 L, & 250-263 M from about 5% - 25%. Note on report says: CANT ACCESS D.S. MH DM-2 DUE TO FENCE, CLEANED LINE BACKWARDS NO D.S. DEPTH | 1983 | 41
269 | EASEMENT | L-4 | DM-2 |  | DM-1 | 194 | 196.8 | 8 | PVC | 0.46% | 2021 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 1 | 0 | 0 | 20 | RC3 | UPSTREAM// Sags @ 0-25 L, 53-75 L, 93-106 L, & throughout 113-195 end M. Egging throughout: joints @ 87 L, 100 L, 113 L, 126 L, 133 L (tap), 139 L, 151 L, 164 L, 176 L, 189 L. Note says: UPSTREAM MH DM-2 IS UNDER A FENCE, NO ACCESS, NO DEPTH | 1983 | 41
270 | W 56TH AVE | M-4 | DM-1 |  | BE-53 | 363 | 367.1 | 10 | P.E. | 0.23% | 2021 | - | 0 | 0 | 0 | 0 | 40 | 10 | 0 | 0 | 4 | 0 | 0 | 50 | REG3 | Deposits/encrustation throughout. Water line is high (about 75%): seems like a sag from 20-114 M, also from 271-367 (MH). Camera under water from 293-300 & 340 until jetting comes back E. Note says: 4 BUCKETS OF DEBRIS REMOVED FROM LINE | -
271 | W 56TH AVE | M-4 | BE-53 |  | BE-52A | 288 | 288.7 | 10 | P.E. | 0.23% | 2021 | - | 0 | 0 | 0 | 0 | 20 | 10 | 0 | 0 | 3 | 0 | 0 | 30 | REG3 | Pipe about 25% full until 38', sag from approx. 50-59 L, 100-165 M, 180-215 L, 224-to end 288 E. Deposits/encrustation throughout L. Note says: 3 BUCKETS OF DEBRIS REMOVED FROM LINE | -
272 | CLAY ST | M-4 | BE-52C |  | BE-52B | 397 | 399.7 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
273 | CLAY ST | M-4 | BE-52B |  | BE-52A | 242 | 245.1 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
274 | W 56TH AVE | M-4 | BE-52A |  | BE-52 | 118 | 115.8 | 10 | P.E. | - | 2021 | - | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 20 | 2 | 0 | 0 | 70 | REG3 | Sag 47-69 E. Failing sealing ring @ 69 E. Note says: 3 BUCKETS OF DEBRIS REMOVED FROM LINE | -
275 | W 56TH AVE | M-4 | BE-52 |  | BE-51 | 408 | 412 | 10 | P.E. | 0.23% | 2021 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 7 | 0 | 0 | 20 | REG3 | Possible sags @ 49-60, 94-105, 166-204, 233-255, 377-405: all L. Possible egging @ 8-20, 100-115, 204-220, 270-340: all L. Note says: 3 BUCKETS OF DEBRIS REMOVED FROM LINE | -
276 | W 56TH AVE | M-4 | BE-51 |  | BE-50 | 140 | 140.1 | 10 | P.E. | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 1 | 0 | 0 | 10 | REG3 | Deposits/encrustation through out L. Water level is about the same through out the pipe. Note says: 2 BUCKETS OF DEBRIS REMOVED FROM LINE | -
277 | W 56TH AVE | M-4 | BE-50 |  | BE-49 | 264 | 262.5 | 10 | P.E | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
278 | W 56TH AVE | M-4 | BE-49 |  | BE-49A | 363 | 365.8 | 10 | P.E. | 0.23% | 2021 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 0 | 0 | 10 | REG3 | Possible sagging throughout L. | -
279 | W 56TH AVE | M-4 | BE-49A |  | BE-49B | 18 | 16.4 | 10 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
280 | W 56TH AVE | L-5 | STUB |  | BE-49B | 255 | 254.9 | 8 | VCP | 0.68% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
281 | EASEMENT | OUT OF DISTRICT | AR-2G |  | AR-2F | 45 | 45 | 8 | PVC | 5.83% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
282 | EASEMENT | OUT OF DISTRICT | AR-2F |  | AR-2E | 90.5 | 90.5 | 8 | PVC | 4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
283 | EASEMENT | OUT OF DISTRICT | AR-2E |  | AR-2D | 57.5 | 57.5 | 8 | PVC | 2% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
284 | EASEMENT | OUT OF DISTRICT | AR-2D |  | AR-2C | 65.6 | 65.6 | 8 | PVC | 2% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
285 | EASEMENT | OUT OF DISTRICT | AR-2C |  | AR-2B | 58.3 | 58.3 | 8 | PVC | 2% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
286 | EASEMENT | OUT OF DISTRICT | AR-2B |  | AR-2A | 76 | 76 | 8 | PVC | 1.81% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
287 | EASEMENT | OUT OF DISTRICT | AR-2A |  | AR-2 | 91.7 | 91.7 | 8 | PVC | 2% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
288 | W 53RD AVE | OUT OF DISTRICT | AR-10 |  | AR-9 | 30.2 | 30.2 | 8 | PVC | 3.67% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
289 | W 53RD AVE | OUT OF DISTRICT | AR-9 |  | AR-8 | 43.5 | 43.5 | 8 | PVC | 2.11% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
290 | W 53RD AVE | OUT OF DISTRICT | AR-8 |  | AR-7 | 53.9 | 53.9 | 8 | PVC | 2.11% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
291 | W 53RD AVE | OUT OF DISTRICT | AR-7 |  | AR-6 | 79 | 79 | 8 | PVC | 2.11% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
292 | EASEMENT | OUT OF DISTRICT | AR-6E |  | AR-6D | 125 | 125 | 8 | PVC | 0.6% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
293 | EASEMENT | OUT OF DISTRICT | AR-6D |  | AR-6C | 78 | 78 | 8 | PVC | 0.6% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
294 | EASEMENT | OUT OF DISTRICT | AR-6C |  | AR-6B | 74 | 74 | 8 | PVC | 0.6% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
295 | EASEMENT | OUT OF DISTRICT | AR-6B |  | AR-6A | 43 | 43 | 8 | PVC | 0.6% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
296 | EASEMENT | OUT OF DISTRICT | AR-6A |  | AR-6 | 50 | 50 | 8 | PVC | 0.6% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
297 | EASEMENT | OUT OF DISTRICT | AR-6 |  | AR-5 | 37.9 | 37.9 | 8 | PVC | 2.11% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
298 | EASEMENT | OUT OF DISTRICT | AR-5 |  | AR-4 | 117.7 | 117.7 | 8 | PVC | 3.43% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
299 | EASEMENT | OUT OF DISTRICT | AR-4 |  | AR-3 | 99.6 | 99.6 | 8 | PVC | 1.54% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
300 | EASEMENT | OUT OF DISTRICT | AR-3 |  | AR-2 | 101.7 | 101.7 | 8 | PVC | 1.49% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
301 | PRIMROSE LN | OUT OF DISTRICT | AR-2 |  | AR-1 | 161.2 | 161.2 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
302 | PRIMROSE LN | L-4 | AR-1 |  | C-2B-2 | 187.4 | 187.4 | 6 | PVC | 5.5% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
303 | PRIMROSE LN | L-4 | C-2B-2 |  | C-2B-1 | 290 | 288.4 | 8 | PVC | 4.15% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
304 | PRIMROSE LN | L-4 | C-2B-1 |  | C-2B | 83 | 82.1 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
305 | COLUMBINE RD | L-4 | C-2F |  | C-2E-1 | 61 | 59 | 8 | PVC | 2% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
306 | COLUMBINE RD | L-4 | C-2E-1 |  | C-2E | 59 | 58.2 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
307 | COLUMBINE RD | L-4 | C-2E |  | C-2D-1 | 128.8 | 128.8 | 8 | VCP | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | REG3 | NO COMMENTS | -
308 | COLUMBINE RD | L-4 | C-2D-1 |  | C-2D | 96.9 | 96.9 | 8 | VCP | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | RC3 | NO COMMENTS | -
309 | COLUMBINE RD | L-4 | C-2D |  | C-2C | 58 | 58 | 8 | VCP | 2% | 2017 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG3 | Deposits/encrustation attached throughout L. | -
310 | W 54TH AVE | L-4 | STUB |  | C-2C | 10 | 10 | 8 | VCP | 4% | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 |  | -
311 | W 54TH AVE | L-4 | C-2C |  | C-2B | 266 | 259.9 | 8 | CIP | 4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | Lined in 2023 | -
312 | W 54TH AVE | L-4 | C-2B-4 |  | C-2B-3 | 121 | 120.4 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
313 | W 54TH AVE | L-4 | C-2B-3 |  | C-2B | 352 | 354.5 | 8 | PVC | 1.26% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
314 | PRIMROSE LN | L-4 | C-2B |  | C-2A-2 | 48.6 | 48.6 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1991 | 33
315 | PRIMROSE LN | L-4 | C-2A-2 |  | C-2A-1 | 191.7 | 191.7 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1991 | 33
316 | PRIMROSE LN | L-4 | C-2A-1 |  | C-2A | 160 | 158.4 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1991 | 33
317 | PRIMROSE LN | L-4 | C-2A |  | C-2 | 332.4 | 332.4 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1991 | 33
318 | COLUMBINE LN | L-4 | C-3A |  | C-3 | 235 | 230.7 | 8 | VCP | 2.51% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 1 | 0 | 0 | 20 | REG3 | UPSTREAM// Localized repair: liner @ 23.9 - 28.0, deposits attached: calcium @ 103.5 M | -
319 | CLAY ST | L-4 | STUB |  | C-3 | 10 | 10 | 8 | VCP | 6.67% | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 |  | -
320 | CLAY ST | L-4 | C-3 |  | C-2 | 249 | 245.1 | 8 | CIP | 6.67% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 2 | 0 | 0 | REG3 | Lined in 2023 | -
321 | CLAY ST | L-4 | C-2 |  | C-1 | 235 | 236.5 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
322 | W 55TH AVE | L-4 | C-1 |  | BR-6-A | 224 | 225.3 | 8 | PVC | 0.4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
323 | W 55TH AVE | L-4 | BR-6A |  | BR-6 | 135.7 | 135.7 | 8 | PVC | 0.4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
324 | LILAC LN | L-4 | D-7 |  | D-8 | 254.5 | 254.5 | 8 | PVC | 0.4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
325 | LILAC LN | L-4 | D-8 |  | D-9 | 253.4 | 253.4 | 8 | PVC | 0.4% | 2021 | - | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 7 | 1 | 0 | 20 | REG3 | Sag @ 223.2 water level increase to approx. 40% M | -
326 | COLUMBINE RD | L-4 | D-9 |  | C-8A | 13 | 12.3 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
327 | COLUMBINE RD | L-4 | STUB |  | C-8B | 6 | 6 | 8 | VCP | - | 2014 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | NO COMMENTS | -
328 | COLUMBINE RD | L-4 | C-8B |  | C-8A | 176 | 174.7 | 8 | VCP | 0.4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | RC3 | NO COMMENTS | 1973 | 51
329 | COLUMBINE RD | L-4 | C-8A |  | C-8 | 30 | 28.6 | 8 | VCP | - | 2021 | - | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | REG3 | Point repair starting @ 26.7 to drop/ offset M. Outside drop @ 27.7 | -
330 | COLUMBINE LN | L-4 | STUB |  | C-15 | 8 | 8 | 8 | PVC | - | 2014 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
331 | COLUMBINE LN | L-4 | C-15 |  | C-14 | 51 | 58.1 | 8 | PVC | 0.93% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
332 | COLUMBINE LN | L-4 | C-14 |  | C-13 | 152.8 | 152.8 | 8 | PVC | 0.86% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
333 | COLUMBINE LN | L-4 | C-13 |  | C-12 | 27.3 | 27.3 | 8 | PVC | 0.81% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
334 | COLUMBINE LN | L-4 | C-12 |  | C-11 | 147 | 144.2 | 8 | PVC | 0.53% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
335 | COLUMBINE LN | L-4 | C-11 |  | C-10 | 116.2 | 116.2 | 8 | PVC | 0.44% | 2021 | - | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 10 | REG3 | Joint: offset @ 67 L | -
336 | COLUMBINE LN | L-4 | C-10 |  | C-9 | 91 | 90.1 | 8 | PVC | 0.39% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
337 | COLUMBINE LN | L-4 | C-9 |  | C-8 | 57 | 56.1 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
338 | EASEMENT | L-4 | C-8 |  | C-5E | 104 | 103 | 8 | PVC | 0.56% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
339 | EASEMENT | L-4 | C-5E |  | C-5D | 12.8 | 12.8 | 8 | PVC | 1.46% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
340 | EASEMENT | L-4 | C-5D |  | C-5C | 40.3 | 40.3 | 8 | PVC | 1.03% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
341 | EASEMENT | L-4 | C-5C |  | C-5B | 177 | 174.8 | 8 | VCP | 5.4% | 2021 | - | 0 | 20 | 10 | 0 | 0 | 10 | 0 | 0 | 2 | 1 | 0 | 40 | REG3 | Break in bottom of joint @ 42.9 L. Deposits/encrustation thorughout L. Material change to PVC @165.2 to 173.8/ offset L; reduced size for approx 3' @ 173.8 going into MH | 1973 | 51
342 | ROSEMARY LN | L-4 | C-5B-1 |  | C-5B | 239.6 | 239.6 | 8 | PVC | 0.5% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
343 | ROSEMARY LN | L-4 | C-5B |  | C-5A | 63.8 | 63.8 | 8 | PVC | 0.9% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
344 | ROSEMARY LN | L-4 | C-5A |  | C-5 | 203 | 200.7 | 8 | PVC | 0.8% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
345 | COLUMBINE LN | L-4 | STUB |  | C-7 | 22.7 | 22.7 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
346 | COLUMBINE LN | L-4 | C-7 |  | C-6 | 126 | 124.9 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
347 | COLUMBINE LN | L-4 | C-6 |  | C-5 | 128.6 | 128.6 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
348 | COLUMBINE LN | L-4 | C-5 |  | C-4 | 337 | 334.9 | 8 | PVC | 2.32% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
349 | W 54TH AVE | L-4 | C-4 |  | BR-8-1 | 202 | 200.2 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
350 | W 54TH AVE | L-4 | BR-8-1 |  | BR-8 | 23 | 20.1 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
351 | ROSEMARY LN | L-4 | STUB |  | BR-8B | 10 | 10 | 8 | VCP | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 |  | -
352 | ROSEMARY LN | L-4 | BR-8B |  | BR-8A | 310 | 9.1 | 8 | VCP | - | 2021 | - | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | RC3 | Couldn't pass point repair & BR-8A has been paved over????/ Could not survey | -
353 | W 54TH AVE | L-4 | BR-8A |  | BR-8 | 128 | 127 | 7 | RL | 2.28% | 2021 | - | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | RC3 | Plastic scrap from joint in pipe @ approx. 5', sag @ 121.1 M | 1976 | 48
354 | BRYANT ST | L-4 | BR-8 |  | BR-7 | 302 | 298.3 | 8 | PVC | 4% | 2021 | - | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 50 | REG3 | Up Stream; No Comments; BR-8-1 connection into MH has infil: runner M | -
355 | BRYANT ST | L-4 | BR-7 |  | BR-6 | 331 | 327.8 | 8 | CIP | 4.6% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | Lined in 2023 | 1976 | 48
356 | W 55TH AVE | L-4 | BR-6 |  | B-1C | 301.6 | 161.4 | 8 | VCP | 0.4% | 2023 | 5-15% | 20 | 0 | 0 | 10 | 20 | 20 | 10 | 0 | 4 | 0 | 0 | 80 | H/RC3 | 5.9 Infiltration: Dripper Connection L/deposits/encrustation M, joint @ 6.6 appears to also have deposits/encrustation M & possible infiltration stain L, 7.4 Multiple Cracks with deposits/encrustation M & possible infil stain L, 56.7 Deposits Attached Encrustation M, tap 78 has Roots Ball Lateral E. Sag from 140-161 M. 144.3 circumferential crack L. Deposits/encrustation throughout L | 1976 | 48
357 | W 55TH AVE | L-4 | B-1C |  | B-1 | 153.9 | 153.9 | 8 | PVC | 0.4% | 2021 | - | 0 | 0 | 25 | 0 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 45 | REG3 | Material change @ 3.0: PVC offset M, material change @ 146.3: VCP. Deposits throughout L. Possible sag @ 120-150 M | 1976 | 48
358 | BEACH CT | L-4 | STUB |  | B-2 | 151 | 151 | 8 | VCP | 6.92% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | RC3 | NO COMMENTS | -
359 | BEACH CT | L-4 | B-2 |  | B-1 | 312.4 | 356.1 | 8 | VCP | 3.88% | 2023 | 5-10% | 0 | 0 | 0 | 10 | 0 | 10 | 10 | 0 | 7 | 1 | 0 | 30 | H/RC3 | Roots throughout in joints L except: 11.1 Roots Medium Joint. Debris/encrustation throughout L. 262.8 Crack Circumferential L. 349-354 Point Repair: Liner. 354.3ft inside drop connection | -
360 | W 55TH AVE | L-4 | B-1 |  | A-3 | 327 | 332.2 | 8 | VCP | 0.4% | 2021 | - | 0 | 0 | 25 | 0 | 20 | 0 | 0 | 0 | 4 | 0 | 0 | 45 | REG3 | Localized repair: liner @ 49.6 - 53.1, material change: PVC 162.8 offset M, material change @ 170.6 VCP. Possible sag @ 18-52 M. | 1976 | 48
361 | W 54TH AVE | L-4 | A-5A |  | A-5 | 147.1 | 147.1 | 8 | PVC | 1.58% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
362 | ALCOTT ST | L-4 | A-5 |  | A-4 | 257.2 | 257.2 | 8 | PVC | 4.73% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | REG3 | Inside drop in A-4. A-4 has cracks and a hole under stairs that have roots coming through L. | -
363 | ALCOTT ST | L-4 | A-4 |  | A-3 | 401 | 405 | 8 | PVC | 4.71% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | RC3 | NO COMMENTS | -
364 | W 54TH AVE | L-4 | A-3A |  | A-3 | 193 | 193.5 | 8 | VCP | 0.4% | 2021 | - | 0 | 0 | 0 | 10 | 10 | 10 | 10 | 0 | 3 | 0 | 0 | 40 | REG3 | Inside drop 193.4. Deposits throughout L; except near tap @ 90.4 M. Crack next to tap @ 1.6 w/roots L. Possible sag @ 9-34 L, 38-58 L, 61-87 L, & 147-169 L. Possible canidate for lining aside from sags. | 1976 | 48
365 | ALCOTT ST | L-4 | A-3 |  | A-2 | 271 | 268.8 | 8 | CIP | 0.56% | 2021 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 3 | 0 | 0 | 20 | REG3 | Looks lined: liner rough at upstream MH, damage at top of line @ approx. 217.5. Tap 98.8 @ 10 (break-in) w/roots: liner cut in wrong spot so tap is 90% covered/ NEEDS FIXED. Possible sags @ 116-140 L, 153-168 L, 175-182 L, 190-202 M, 220-232 L, 254-266 M. | 1976 | 48
366 | ALCOTT ST | L-4 | A-2 |  | A-1 | 402 | 401.9 | 8 | VCP | 3.36% | 2021 | - | 0 | 0 | 25 | 10 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 35 | RC3 | Roots in joint @ approx. 29, 44, 49, 75, 85, 146, 171, 176, 181, 196, 201, 206, 211, 221, 236, 273, 294, 299, 309, 314, 319, 324, 344, 354, 370, 380 all L. Point repair: PVC @ apprx. 389-392 off set on 389 joint M. Possible canidate for lining aside from the off set and sag at the end. | 1976 | 48
367 | W 56TH AVE | M-4 | A-1 |  | A-1A | 160 | 157 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
368 | CLAY ST | M-4 | CL-5 |  | CL-4 | 108 | 106.9 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 3 | 0 | 0 | 10 | REG3 | Some deposits attached L. | -
369 | CLAY ST | M-4 | CL-4 |  | CL-3 | 403 | 399.8 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 10 | 0 | 0 | 20 | REG3 | Some deposits attached L. Possible sag 38-396 L | -
370 | CLAY ST | M-4 | CL-3 |  | CL-2 | 388 | 386.8 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 10 | 0 | 0 | 20 | REG3 | Some deposits attached L. Possible sag 325-332 L | -
371 | CLAY ST | M-4 | CL-2 |  | CL-1 | 83 | 80.6 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 2 | 0 | 0 | 10 | REG3 | Possible Sag 30-40 L, 70-79 L | -
372 | W 58TH AVE | M-4 | CL-1 |  | BR-1 | 126 | 125.9 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 3 | 0 | 0 | 20 | REG3 | UPSTREAM: Some deposits attached L. Possible sags @ 0-16 L, 22-30 L, 47-65 L, | -
373 | BRYANT ST | M-4 | BR-5 |  | BR-4 | 111 | 111.4 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 3 | 0 | 0 | 10 | REG3 | UPSTREAM: Some deposits attached L. | -
374 | BRYANT ST | M-4 | BR-4 |  | BR-3 | 146 | 145 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
375 | BRYANT ST | M-4 | BR-3 |  | BR-2 | 399 | 396.8 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 11 | 0 | 0 | 10 | REG3 | Some deposits attached L. | -
376 | BRYANT ST | M-4 | BR-2 |  | BR-1 | 394 | 393.9 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 10 | REG3 | UPSTREAM: Some deposits attached L. | -
377 | W 58TH AVE | M-4 | BR-1 |  | A-1D | 225 | 224.3 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 4 | 0 | 0 | 20 | REG3 | Slight sag 10-20 L, 34-41 L, 74-84 L, 105-115 L, 217-137 L, 147-167 L, 211-223 M. Some deposits attached L | -
378 | TEJON ST | L-3 | D-4A |  | D-4 | 194 | 192.4 | 8 | VCP | 2.1% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 10 | 3 | 0 | 0 | 40 | REG1 | Possible infil stain in joint @ 20, 35, 65, 105, 116, 126, 131, 136, 156, 170, 186; no infil observed. Deposits/encrustation through out L except 116-131 M. Deterioration through out L. Possible crack 68-70 @ 10 L. Possible candidate for lining | -
379 | W 52ND PL | L-3 | D-6 |  | D-5 | 372 | 369 | 8 | PVC | 4.95% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 8 | 0 | 0 | 10 | REG1 | Some deposits attached L. | -
380 | W 52ND PL | L-3 | D-5 |  | D-4 | 225 | 222.8 | 8 | VCP | 2.16% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 5 | 0 | 0 | 20 | REG1 | Crack 155 @ 12 L. Possible infil stain in joint @ 174, 189, 200, 210, 215; no infil observed. Deposits through out L.Point repair PVC @ 203-208. Possible candidate for lining | -
381 | TEJON ST | L-3 | D-4 |  | D-3 | 278 | 277.8 | 8 | CIP | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 0 | 0 | 10 | REG1 | UPSTREAM: Lined; Possible sag from 0-20 M, 27-42 L, 56-70 L, 76-94 L, 100-125 L, 130-168 L, 247-275 M | -
382 | W 52ND AVE | L-3 | D-3D |  | D-3C | 121 | 120.6 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG1 | NO COMMENTS | -
383 | W 52ND AVE | L-3 | D-3C |  | D-3B | 90 | 88.6 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG1 | Some deposits attachedL. Outside drop @ 88.6 | -
384 | W 52ND AVE | L-3 | D-3B |  | D-3A | 399 | 395 | 8 | VCP | 4.8% | 2022 | - | 20 | 0 | 0 | 10 | 0 | 10 | 10 | 0 | 6 | 0 | 0 | 50 | RC1 | Some depoits through out L. Possible roots in joint @ 15.1 L, 19.9 L, 25.1 L, 30.1 L, 35.0 L, 40.0 L, 45.0 L, 74.6 M, 210.4 L. Possible Infil in joint @ 84.8 L, 100.0 L, & 114.7 L. Crack 134.9 @ 2 L & 348.3 @ 2 L. Possible candidate for lining | -
385 | W 52ND AVE | L-3 | D-3A |  | D-3 | 200 | 198.4 | 8 | VCP | 4.69% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 2 | 0 | 0 | 20 | REG1 | Deposits/grease attached throughout but heavy in some spots 72.8 & 92.5-176.4 M Possible candidate for lining | -
386 | W 52ND AVE | L-3 | D-3 |  | D-2 | 250 | 246.9 | 8 | VCP | 2.64% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 40 | REG1 | UPSTREAM: Deposits/grease attached throughout but heavy in some spots 5-26 & 55-110 Possible candidate for lining | -
387 | W 52ND AVE | L-3 | D-2 |  | D-1 | 21 | 20.5 | 8 | VCP | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | UPSTREAM: Looks like quite a bit of grit. Deposits attached M. Possible candidate for lining | -
388 | ZUNI ST | L-3 | STUB |  | Z-26 | 10 | 10 | 8 | VCP | 2.2% | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 |  | -
389 | ZUNI ST | L-3 | Z-26 |  | Z-25 | 328 | 324.4 | 8 | VCP | 2.2% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG1 | UPSTREAM: Encrustation/deposits through out L. Possible candidate for lining | -
390 | ZUNI ST | L-3 | Z-25 |  | Z-24 | 297 | 296.9 | 8 | CIP | 0.6% | 2022 | - | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | Sags @ 28-49 L, 54-75 L, 77-100 L, 114-125 L, 133-142 L, 185-207 L, 221-228 L, 272-294 M. Lined in 2023 | -
391 | ZUNI ST | L-3 | Z-24 |  | Z-23 | 302 | 300.4 | 8 | VCP | 0.6% | 2022 | - | 0 | 0 | 0 | 0 | 10 | 20 | 10 | 10 | 0 | 0 | 0 | 50 | REG1 | Camera starts out underwater for the first 6 ft; looks like a lot of grit in the bottom of the pipe. Crack/fracture at the bottom of the pipe @ joint 123 L, multiple/spiral fracture from 165-169 M, crack/fracture at the bottom of the pipe @ joint 287 L. Deterioration through out L. Possible sag/high spot from 0-27 L, 48-54 L, 57-61 L, 147-154 M, 157-165 M, 179-190 L, 194-200 L, 206-216 L, 228-236 L, 254-267 L, 276-287 M. Possible candidate for lining | -
392 | ZUNI ST | L-3 | Z-23 |  | Z-22 | 326 | 322.5 | 8 | VCP | 5.08% | 2022 | - | 20 | 20 | 10 | 10 | 0 | 0 | 10 | 10 | 7 | 0 | 0 | 80 | RC1 | Point repair 175-180: offset @ 175 L. Possible infil in joint @ 1 L, 61 L, 66 L, 82 L, 94 L, 175 L, 189 L, 211 L, 235 L, 260 L, 280 L, 296 L, 306 L. Egging/deformed around tap 177.3 L. Roots in joint @ 81 L, 87 L, 133 L, 139 L, 142 L, 148 L, 168 L, 173 L, 183 L, 188 L, 194 L, 199 L, 204 L, 209 L, 214 L, 219 L, 224 L, 229 L, 234 L. Crack in joint 132 L, broken/missing piece @ top of joint 194 L. Possible candidate for lining | 1973 | 51
393 | ZUNI ST | L-3 | Z-22 |  | Z-21 | 330 | 327.8 | 8 | CIP | 7.2% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | REG1 | Lined in 2023 | 1973 | 51
394 | ZUNI ST | L-3 | Z-21 |  | Z-20 | 275.7 | 273.4 | 8 | VCP | 4.08% | 2022 | - | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 10 | 1 | 0 | 0 | 50 | REG1 | UPSTREAM; Infil stain around joint 12 @ 2 L, 38 @ 2 L, 42 circumference of pipe L, 94 @ 10 L, 114 circumference of pipe L, 105 @ 10 L, 170 circumference of pipe L, 195 circumference of pipe L, 211 both sides of pipe L, 246 @ 10 L. Encrustation @ 36.9 top of pipe L, 94.8 top of pipe M, 115.7 top of pipe L, 117.9 top of pipe L, 121.7 top of pipe L, 125.4 top of pipe L, at joint 160 possible infil M. Some deterioration throughout pipe L. Possible candidate for lining | 1973 | 51
395 | ZUNI ST | L-3 | Z-20 |  | Z-19 | 376.3 | 374.1 | 8 | VCP | 4.08% | 2022 | - | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 2 | 0 | 0 | 20 | REG1 | Point repair: PVC @ 176 offset L, unknown object protruding from the bottom of the pipe; not sure if in joint 299/camera can pass over it. | 1973 | 51
396 | ZUNI ST | L-3 | Z-19 |  | Z-18 | 25 | 23.4 | 8 | VCP | 4.08% | 2018 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 1973 | 51
397 | W 56TH AVE | M-4 | BE-49B |  | Z-18 | 51 | 50 | 8 | VCP | - | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 0 | 10 | 0 | 2 | 0 | 0 | 30 | REG1 | Point repair: PVC 0-4, offset/seperated joint @ 4 L. Sag 37-47 L. 47.1 ft. Crack Circumferential L | -
398 | EASEMENT | L-3 | STUB |  | T-8H | 5 | 5 | 8 | PVC | - | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | (televising didn't go into stub but end can be seen from MH, not taps) | -
399 | EASEMENT | L-3 | T-8H |  | T-8G | 98 | 95.7 | 8 | PVC | 1% | 2023 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS. COULD BE ABANDONED/NO TAPS | 1972 | 52
400 | EASEMENT | L-3 | T-8G |  | T-8F | 45 | 44.7 | 8 | VCP | 1% | 2023 | 10% | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | Roots in joint @ 9.9 L, sag 12-20 L, Circumferential crack 21.8 L. COULD BE ABANDONED/NO TAPS | 1972 | 52
401 | EASEMENT | L-3 | T-8F |  | T-8E-1 | 126 | 83.1 | 8 | VCP | 2.8% | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 2 | 0 | 0 | 10 | RC1 | Invert in MH T-8F is deteriorated; needs fixed. Crack at tap 19.2 L. | -
402 | EASEMENT | L-3 | T-8E-4 |  | T-8E-3 | 127 | 125.3 | 8 | PVC | 0.75% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2019 | 5
403 | EASEMENT | L-3 | T-8E-3 |  | T-8E-2 | 190 | 189.3 | 8 | PVC | 0.75% | 2023 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2019 | 5
404 | EASEMENT | L-3 | T-8E-2 |  | T-8E-1 | 51 | 51.2 | 8 | PVC | 0.75% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS | 2019 | 5
405 | EASEMENT | L-3 | T-8E-1 |  | T-8E | 50 | 40 | 8 | VCP | 2.8% | 2022 | - | 0 | 0 | 10 | 10 | 0 | 0 | 10 | 0 | 1 | 0 | 0 | 30 | RC1 | UPSTREAM: Possible crack at top of pipe @ 35 L. Off set joint @ 1 M. Roots in joint @ 1 L. | 2019 | 5
406 | W 53RD AVE | L-3 | T-8E |  | T-8D | 300 | 298.2 | 8 | VCP | 2.8% | 2021 | - | 20 | 0 | 25 | 10 | 0 | 10 | 10 | 10 | 8 | 0 | 0 | 85 | RC1 | UPSTREAM: Joints offset throughout: 1 L, 8 L, 14 L, 23 L, 39 L, 44 L, 49 L, 59 M, 68 L, 74 M, 79 L, 84 L, 94 L, 99 L, 104 L, 109 L, 119 L, 124 L, 129 M, 134 L, 139 M, 149 L, 154 M, 159 L, 169 L, 171 L, 179 M, 184 L, 189 L, 199 L, 204 M, 214 L, 219 L, 224 M, 229 L, 234 L, 249 L, 255 M, 260 L, 270 M, 280 M, 285 L, 290 L. Roots in joints @ 24 L, 44 L, 49 L, 59 L, 74 L, 79 L, 89 L, 99 L, 104 L, 109 L, 119 L, 129 L, 139 L, 154 L, 159 L, 185 L, 189 L, 194 L, 199 M, 205 L, 209 L, 214 L, 229 L, 249 L, 254 L, 264 L, 269 L, 274 L, 284 L, 299 L. Deterioration @ 164 L in joint. Deposits attached through out L. Possible circumferential crack @ 156 L, 167 L, 212 L, 246 L, 282 L. Possible infil in joint @ 34 L, 44 L, 49 L, 64 L, 69 L, 94 L, 99 L, 104 L, 109 L, 124 L, 129 L, 134 L, 154 L, 174 L, 184 L, 199 L, 214 L, 224 L. | 1978 | 46
407 | W 53RD AVE | L-3 | T-8D |  | T-8C | 347 | 342 | 8 | VCP | 3.8% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | RC1 | Lined from 317-321. NO COMMENTS. Possible candidate for lining | 1978 | 46
408 | VALLEJO WAY | L-3 | STUB |  | T-8C2 | 10 | 10 | 8 | PVC | * | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS | -
409 | VALLEJO ST | L-3 | T-8C2 |  | T-8C1 | 60 | 69.5 | 8 | PVC | * | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS | -
410 | VALLEJO ST | L-3 | T-8C1 |  | T-8C | 200 | 268.6 | 8 | PVC | * | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS | -
411 | W 53RD AVE | L-3 | T-8C |  | T-8B | 172 | 173.8 | 8 | VCP | 2.6% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS | 1978 | 46
412 | W 53RD AVE | L-3 | T-8B |  | T-8A | 323 | 323.8 | 8 | VCP | 2.48% | 2023 | 5% | 20 | 0 | 0 | 10 | 0 | 10 | 10 | 10 | 4 | 0 | 0 | 60 | RC1 | Roots 188.6 L, 198.6 L, 208.7 L. Circumferential crack 78.6 L, 203 L, 316.2 L, 318.3 L ;Root cut saw marks thorughout L. Deposits/encrustation throughout L. Possible infil in bottom of pipe 173.7 L, 178.8 L, 183.9 L, 233.5 L. | 1978 | 46
413 | W 53RD AVE | L-3 | T-8A |  | T-8 | 320 | 318.4 | 8 | VCP | 1.6% | 2022 | - | 0 | 0 | 25 | 10 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 35 | REG1 | Upstream: Joint offset: 39 L, 44 L, 55 L, 60 L, 65 M, 70 M, 75 M, 80 M, 85 L, 90 L, 95 M, 100 L, 110 M, 115 M, 120 M, 125 M, 140 L, 170 L, 175 M, 215 L. Roots in joint @ 134 L. Possible candidate for lining | 1978 | 46
414 | TEJON ST | L-3 | T-8 |  | T-7 | 311 | 309.1 | 8 | VCP | 0.4% | 2022 | - | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 6 | 0 | 0 | 20 | REG1 | Joint slight offset 15 L, 23 L, 38 L, 52 L, 62 L, 77 L, 106 L, 122 L, 141 L, 162 L, 176 l, 181 L, 208 L, 218 L, 228 L, 239 L, 263 L, 268 L, 274 L. Possible sag @ 30-38 L, 59-66 L, 92-101 L, 119-126 L, 143-151 L, 257-268 L, 280-308 M | 1978 | 46
415 | TEJON ST | L-3 | T-7 |  | T-6 | 311 | 309.3 | 8 | VCP | 2.24% | 2019 | - | 20 | 0 | 10 | 10 | 0 | 0 | 10 | 0 | 5 | 0 | 0 | 50 | RC1 | Roots in joint: 177.2 L, 187.1 L, 242.1 L. Offset joints: 302.4 L, 305.3 M. Multiple fractures 198.4-201.1 L. Possble infil bottom of joint 272.3 L. | 1978 | 46
416 | TEJON ST | L-3 | T-6 |  | T-5 | 52 | 49.5 | 8 | VCP | 3% | 2023 | 5% | 0 | 0 | 10 | 10 | 20 | 10 | 0 | 0 | 0 | 0 | 0 | 50 | REG1 | Sag 8-19 M, roots 42.7 L. Depoits/Encrustation throughout L. Joint offset 32.6. | -
417 | TEJON ST | L-3 | T-5 |  | T-4 | 330 | 332.9 | 8 | VCP | 3% | 2021 | - | 0 | 0 | 10 | 0 | 10 | 10 | 0 | 10 | 8 | 0 | 0 | 40 | RC1 | Deterioration/pitting: 0.0 hole L. Egged/deformed @ joint 15 L, 20 L, 46 L, 107 L, 113 L, 164 L. Off set joint @ 93 L, 103 L, 113 L, 118 L, 127 L, 158 L, 164 L, 184 L, 240 L, 292 L, 307 L. Sag @ 255-261 L. Calcium buildup on top of pipe @ joint 322 & 327 L. High water level at end of pipe going into MH. | -
418 | W 53RD PL | L-3 | W-6A |  | W-6 | 253 | 251.6 | 8 | CIP | 2.39% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | REG1 | Lined in 2023 | -
419 | WYANDOT ST | L-3 | W-6 |  | W-5 | 68 | 65.7 | 8 | VCP | 0.4% | 2023 | 5% | 0 | 0 | 0 | 25 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | REG1 | Roots 30.9 L, 35.1 L, 40.3 L, 61.5 L. Sag 33.4-61.5 L. Roots in MH W-5 M. | -
420 | WYANDOT ST | L-3 | W-5 |  | W-4 | 341 | 337.1 | 8 | VCP | 5.64% | 2022 | - | 20 | 0 | 10 | 25 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 65 | RC1 | Roots in joint @ 181M, 191 M, 199 L, 223 L, 233 M, 239 M, 241 M, 289 L; All cut. Possible infil in the joint @ 13 L, 18 L, 23 L, 28 L, 53 L, 73 L, 78 L, 83 L, 118 L. Joints offset @ 28 L, 58 L, 68 L, 128 L, 148 L, 153 L, 158 L, 168 L, 173 L, 178 L, 183 L, 188 L, 193 L, 208 L, 213 L, 223 L, 248 L, 283 L, 313 L, 323 L. Possible circumferential crack @ 74 L, 105 L. | -
421 | W 54TH AVE | L-3 | W-4A |  | W-4 | 132 | 191.2 | 8 | VCP | 4.32% | 2023 | 5% | 20 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 4 | 0 | 0 | 30 | REG1 | UPSTREAM: Point Repair: PVC 80.9-85.6. Deposit/encrustation around joint; possible infil 3 L, 40.2 L. Possible infil in bottom of joint 5 L, 24.9 L, 35.3 L. | 1972 | 52
422 | W 54TH AVE | L-3 | W-4 |  | V-10 | 362 | 357.5 | 8 | VCP | 0.56% | 2022 | - | 0 | 20 | 10 | 0 | 20 | 20 | 10 | 0 | 6 | 1 | 0 | 80 | REG1 | Deposits/encrustation at beginning of pipe M, aroung tap @ 54.9 M, deposits/encrustation through out rest of pipe L. Sag @ 17-24 L, 49-60 L, 79-90 L, 93-106 L, 111-115 L, 119-141 L, 160-185 M, 190-200 L, 211-216 L, 233-256 M, 276-285 M, 291-296 L, 308-332 M, 349-355 L. Off set joint @ 119 L, 155 L, 210 L, 225 L, 235 L, 270 L, 280 L, 285 L, 350 L. Broken 291.4 @ 2 L. Circumferential Crack 353.7 L. | 1972 | 52
423 | VALLEJO ST | L-3 | STUB |  | V-12 | 5 | 5 | 8 | PVC | * | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | NO COMMENTS/NOT VIDEOED TO END | -
424 | VALLEJO ST | L-3 | V-12 |  | V-11 | 180 | 185.8 | 8 | PVC | 1.4% | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 0 | REG1 | NO COMMENTS | -
425 | VALLEJO ST | L-3 | V-11 |  | V-10 | 101 | 97.8 | 8 | PVC | 10.29% | 2022 |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 2 | 0 | 0 | 10 | REG1 | Some deposits attached L. NO COMMENTS | -
426 | VALLEJO ST | L-3 | V-10 |  | V-9 | 338 | 334.3 | 8 | VCP | 5.1% | 2022 | - | 20 | 0 | 25 | 10 | 0 | 0 | 10 | 0 | 7 | 0 | 0 | 65 | REG1 | Joint offset @ 2.2 M, 5 M, 35 L, 45 L, 50 L, 60 L, 75 L, 86 L, 127 L, 157 L, 172 L, 182 L, 207 L, 222 L, 227 L, 232L, 253 M, 298 M. Crack @ joint 2.2 L, around tap 244 L, @ joint 192, 323, & 328 L. Possible infil in joint @ 35 L, 45 L, 50 L, 60 L, 75 L, 86 L, 112 L, 122 L, 127 L, 152 L, 157 L, 162 L, 167 L, 172 L, 182 L, 192 L, 207 L, 222 L, 227 L, 232 L, 253 L, 278 L, 293 L, 298 L, 303 L, 323 L. Liner; point repair @ 265-269. Roots in joints @ 102 L, 107 L, 162 L, 283 L, 328 L. Possible candidate for lining. | -
427 | W 54TH PL | L-3 | V-9B |  | V-9A | 253 | 252.2 | 8 | PVC | 0.06% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | REG1 | UPSTREAM: NO COMMENTS | -
428 | W 54TH PL | L-3 | V-9A |  | V-9 | 309 | 309.4 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 7 | 0 | 0 | 10 | REG1 | Possible sag @ 283-289 L. Material change; 305 VCP. | -
429 | W 54TH PL | L-3 | V-9 |  | U-5 | 287 | 282.7 | 8 | VCP | 1.8% | 2022 | - | 0 | 0 | 10 | 0 | 10 | 20 | 0 | 0 | 3 | 0 | 0 | 40 | REG1 | Liner; point repair @ 0-4. Joint off set @ 65 L, 105 L, 111 L, 131 L, 151 L, 165 L, 171 L, 176 L, 226 L, 252 L. Possible sag @ 107-111 L, Deposits/encrustation through out L except @ 189-204 M & 225 M | 1963 | 61
430 | W 54TH AVE | L-3 | U-7A |  | U-7 | 130 | 115.7 | 8 | VCP | 3.75% | 2023 | - | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 0 | 2 | 0 | 0 | 30 | REG1 | Point Repair: Liner 33.2-37.3. Point repair: PVC 74.8-76.8. Roots in joint: 24.2 L, 30 L, 44.2 L, 49.1 L, 54.3 L, 104.6 L, 109.6 L. Deposits/encrustation 74.8-76.8 L. Sag 79-90 L. | -
431 | UMATILLA ST | L-3 | U-7 |  | U-6 | 84 | 84 | 8 | RL | 0.64% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS | -
432 | UMATILLA ST | L-3 | U-6 |  | U-5 | 254 | 106.8 | 8 | RL | 4.36% | 2018 | - | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 75 | REG1 | Damage at the top of the pipe 35.9 M. ABANDONED; UNABLE TO PASS DAMAGE. UPSTREAM; Pipe out of round 70.9 M. ABANDONED; UNABLE TO PASS. | -
433 | W 54TH PL | L-3 | U-5 |  | T-4 | 337 | 336.1 | 6 | RL | 2.12% | 2018 | - | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 3 | 0 | 0 | 20 | REG1 | Intruding sealing ring 0.6 L, sag 165-170 L. | 1963 | 61
434 | TEJON ST | L-3 | T-4 |  | T-3 | 386 | 390.6 | 8 | CIP | 2.72% | 2021 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | REG1 | Sag @ 17-24 L, 139-152 M, 176-183 L, 231-239 L. Deposits in downstream MH (T-3). Lined in 2023 | 1978 | 46
435 | TEJON ST | L-3 | T-3 |  | T-2 | 407 | 415.5 | 8 | PVC | 2.4% | 2019 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 10 | REG1 | Circumferential cracks 1.0 L & 412.6 L. Material change VCP to PVC 0-3.6 & PVC to VCP 411.6-415.5. In good shape aside from the double bends at each end. | 1978 | 46
436 | TEJON ST | L-3 | T-2 |  | T-1 | 218 | 216.5 | 8 | VCP | 2% | 2022 | - | 0 | 0 | 10 | 0 | 10 | 0 | 10 | 0 | 1 | 0 | 0 | 30 | REG1 | Possible sag 9.3-15.4 L, possible sag @ 24.9-30.6 L. Crack 24.0 @ 12 next to joint L, possible crack 44.1 @ 12 next to joint L. Joint offset slightly 69.8 L, 74.6 L, 79.5 L, 94.5 L, 119.6 L, 169.3 L, 174.6 L, 204.3 L. Brick in the invert of downstream, looks like to divert from old invert. | 1978 | 46
437 | W 56TH AVE | L-3 | T-1 |  | U-1 | 333 | 330.9 | 8 | VCP | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 20 | 10 | 10 | 0 | 1 | 0 | 0 | 40 | REG1 | Possible vertical crack 23.6 @ 10 L, possible cracks 46.4 L, possible crack 62.6 L, possible crack 81.0 L, circumferential fracture 174.0 M, possible cracks 255.0 L. Sag @ 56.3-79.0 L, sag @ 81.9-89.9 L, sag @ 96.6-127.0 L, sag @ 134.0-173.0 L, sag @ 181.5-196.3 M, sag @ 201.4-238.1 M, sag @ 241.5-253.0 L, sag @ 256.4-274.1 L, sag @ 284.6-296.3 M, sag @ 299.7-323.0 L. Some deposits attached through out L. | 1976 | 48
438 | UMATILLA ST | L-3 | U-4 |  | U-3 | 378 | 377.5 | 8 | VCP | 2.68% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | REG1 | NO COMMENTS. Good candidate for lining. | -
439 | UMATILLA ST | L-3 | U-3 |  | U-2 | 265 | 262.2 | 8 | VCP | 2.68% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | REG1 | NO COMMENTS. Good candidate for lining. | -
440 | UMATILLA ST | L-3 | U-2 |  | U-1 | 266 | 264.3 | 8 | VCP | 2.68% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG1 | Spoon wedged in joint @ 150.5; not a significant obstruction. Good candidate for lining. | -
441 | W 56TH AVE | L-3 | U-1 |  | W-3C | 200 | 399.5 | 8 | VCP | - | 2023 | 5-20% | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 6 | 1 | 0 | 20 | REG1 | SAG 9-30 M, 34-59 M, 77-119 M, 130-151 M, 161-217 M, 225-233.5 L, 290-309 L, 320-328 M, 335-373 L. MATERIAL CHANGE: PVC 393.5 | -
442 | W 56TH AVE | M-3 | W-3C |  | W-3B | 220 | 219.3 | 12 | PVC | 0.25% | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 0 | 0 | REG1 | NO COMMENTS | -
443 | VALLEJO ST | L-3 | V-8 |  | V-7 | 174 | 173.7 | 8 | VCP | 5.1% | 2022 | - | 0 | 0 | 10 | 0 | 0 | 10 | 10 | 0 | 5 | 0 | 0 | 30 | REG1 | Liner; point repair @ 12.9-16.7. Crack next to tap 17.4 @ 10 L. Depostis/encrustation throughout; joint @ 71, 86, 118 has some calcium build up L. Material change @ 165 PVC; Joint offset M. | -
444 | W 55TH AVE | L-3 | STUB |  | V-7B | 52 | 52.2 | 8 | PVC | - | 2014 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG1 | UPSTREAM; Drop into MH V-7B. Material change: DIP 50.3. NO COMMENTS | -
445 | W 55TH AVE | L-3 | V-7B |  | V-7A | 240 | 240.4 | 8 | PVC | 1.06% | 2023 | 5-10% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 7 | 0 | 0 | 20 | REG1 | Sag 125-142. Egging joints thorughout L. Holding water in the MH V-7A | -
446 | W 55TH AVE | L-3 | V-7A |  | V-7 | 300 | 316.4 | 8 | PVC | 0.4% | 2023 | 5-10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | REG1 | NO COMMENTS | -
447 | VALLEJO ST | L-3 | V-7 |  | V-4 | 338 | 334.7 | 8 | PVC | 2.4% | 2022 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 7 | 0 | 0 | 10 | REG1 | Possible sag @ 100-105 L, 190-200 L, 250-260 L, 300-310 L, 315-325 L | 1973 | 51
448 | W MOFFAT PL | L-3 | V-4 |  | V-4A | 92 | 91.1 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | REG1 | NO COMMENTS | 1973 | 51
449 | W MOFFAT PL | L-3 | V-4C |  | V-4B | 262 | 260 | 8 | PVC | 1% | 2022 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 6 | 0 | 0 | 10 | REG1 | Possible sag @ 137-147 L, 193-202 L, 252-259 L. | -
450 | W MOFFAT PL | L-3 | V-4B |  | V-4A | 253 | 249.1 | 8 | PVC | 0.6% | 2022 | - | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 5 | 0 | 0 | 20 | REG1 | Possible sag @ 230-248 L. Joints egged/deformed @ 126 L, 152 L, pipe around tap @ 168 L, 205 L. | -
451 | W MOFFAT PL | L-3 | V-4A |  | W-3C | 338 | 338 | 8 | P.E. | 3% | 2022 | - | 0 | 0 | 10 | 0 | 10 | 20 | 0 | 0 | 3 | 0 | 0 | 40 | REG1 | Deposits/grease attached throughout M. Egging/deformation @ 108-115 M & joint @ 138 L. Sag @ 232-250 L, 300-315 L. Material change: PVC @ 331. Drop @ 338 | -
452 | W 56TH AVE | M-3 | W-3B |  | W-3 | 275 | 54.7 | 12 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | -
453 | W 56TH AVE | M-3 | STUB |  | W-3A | 50 | 20.4 | 6 | PVC | - | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS | -
454 | W 56TH AVE | M-3 | W-3A |  | W-3 | 190 | 207.8 | 8 | PVC | 0.96% | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | REG1 | OUTSIDE DROP AT 203.5 | 1991 | 33
455 | WYANDOT ST | M-3 | W-3 |  | W-2 | 345 | 347.5 | 8 | VCP | 0.95% | 2023 | 5-15% | 20 | 0 | 0 | 10 | 20 | 0 | 10 | 10 | 4 | 0 | 0 | 70 | H/RC1 | Point repair: PVC 0-5. Roots in joint: 62.2 L, 73.1 L, 78.5 L, 110.3 L, 115.5 L, 142.3 L, 340.5 L. Sag: 30-53 M, 68-79 L, 86-95 L, 137-145 L, 288-315 M. Surface damage/deterioration 5-21 L. Crack top of pipe near joint 151.9 L, 318.9 L. Possible infil in joint 19.6 L, 169.5 L. Point repair: PVC 265.1-273.7. | -
456 | W 56TH PL | M-3 | W-2A |  | W-2 | 285 | 307.9 | 8 | VCP | - | 2023 | 10% | 0 | 0 | 0 | 10 | 40 | 0 | 10 | 0 | 7 | 0 | 0 | 60 | H/RC1 | Roots 150 L, 164.4 L, 222.3 L. Sag 28-97 E, 105-132 M, 150-200 M, 220-250 E, 259-304 E. Crack on 10 side near joint 216.9 L. | -
457 | WYANDOT ST | M-3 | W-2 |  | W-1 | 291 | 290.4 | 8 | VCP | 1.4% | 2023 | 5-15% | 0 | 0 | 10 | 10 | 20 | 0 | 10 | 0 | 5 | 1 | 0 | 50 | H1 | Roots 13.6 L, 18.7 L, 23.7 L, 56.5 L, 71.8 L, 139.6 L, 155.2 L, 160.1 L, 165.1 L, 171 L, 176.1 L, 191.9 L. Sag 88-100 L, 281.8-289.5 M. Encrustation/possible infil in joint 86.3 L. Crack at top of pipe near joint 108.5 L & at tap 262.3 L. Point Repair: PVC 281.6-289.5 offset L. | 1970 | 54
458 | W 57TH PL | M-3 | W-1 |  | V-3 | 318 | 315.6 | 8 | PVC | 0.44% | 2022 | - | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 7 | 0 | 0 | 40 | REG1 | Whole pipe is egged/deformed M, deform/damage @ 74 L. Possible sag @ 41-53 L, 63-97 M, 152-170 L, 211-292 L | -
459 | VALLEJO ST | M-3 | V-3 |  | V-3A | 71 | 68.1 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG1 | NO COMMENTS; DUPLICATE ON 12/7/22 | -
460 | VALLEJO ST | M-3 | V-3A |  | V-2 | 291 | 287.3 | 8 | PVC | 0.68% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG1 | NO COMMENTS; DUPLICATE ON 12/7/22 | -
461 | W 58TH PL | M-3 | V-2A |  | V-2 | 272 | 270 | 8 | VCP | 0.4% | 2021 | - | 0 | 0 | 10 | 10 | 10 | 0 | 10 | 0 | 7 | 3 | 0 | 40 | RC1 | Material change: PVC 255; seperated joint L. Offset joints @ 22 L. Roots in joints @ 12 L, 22 L, 43 L, 47 L, 53 L, 75 L, 91 L, 96 L, 101 L, 106 L, 111 L, 116 L, 121 L, 126 L, 131 L, 136 L, 141 L, 147 L, 152 L, 157 L. Possible sag @ 0-38 L, 116-142 L. Fracture @ 18.7 top of pipe L, 128.7 @ 2 L, crack next to tap @ 170.2 L. POSSIBLE CANIDATE FOR LINING | 1970 | 54
462 | VALLEJO ST | M-3 | V-2 |  | V-1 | 359 | 357.6 | 8 | PVC | 0.68% | 2022 | - | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | Possible sag @ 29-40 M, 86-95 M, 124-132 L, 138-148 L, 200-210 L, 290-300 L, 325-345 M | -
463 | W 59TH PL | M-3 | V-1 |  | Z-12 | 303 | 300.6 | 8 | VCP | 0.4% | 2021 | - | 20 | 20 | 10 | 10 | 10 | 10 | 0 | 0 | 9 | 0 | 0 | 80 | RC1 | Point repair: PVC 0-15 Material change: PVC @ 295. Joint separated or broken @ 15 L w/possible infil L. Joint offset @ 17 L, 47 L, 103 L, 266 L, 271 L. Roots in joint @ 22 L, 27 L, 37 L, 73 L, 82 L, 87 L, 93 L, 98 L, 108 L, 113 L, 123 L, 128 L, 133 L, 145 L, 155 L, 160 L, 165 L, 170 L, 256 L, 283 L. Possible Sag @ 70-78 L, 108-127 L, 160-182 L, 265-296 M. Deposits/encrustation throughout L. Invert in Z-12 Diverted North for some reason; CIP- Remove diversion to flow through to Z-13 & abandon Z-12 -PLP-02 as well as vacate easement if possible. | 1970 | 54
464 | ZUNI ST | L-3 | Z-18 |  | Z-17 | 140 | 142 | 8 | VCP | 1.6% | 2023 | 5% | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 0 | 1 | 0 | 0 | 30 | RC1 | UPSTREAM: Roots joint 1.9 L. Sag 3-17 L, 23-34 L, 50-60 L, 81-90 L, 105-116 L. Deposits/encrustation throughout L. | 1973 | 51
465 | ZUNI ST | M-3 | Z-17 |  | Z-16 | 367 | 365.8 | 8 | VCP | 2.6% | 2023 | 5% | 20 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 4 | 1 | 0 | 40 | H/RC1 | UPSTREAM: Point repair: PVC 0-4.3. Point repair: liner 16-19.9. Roots in joint: 46.2 L, 62.3 L. Possible infil in joint: 72.7 L, 82.9 L, 93.2 L, 98.3 L, 111.6 L, 120.7 L, 125.8 L, 141 L, 166.2 L, 181.5 L, 212.1 L, 219.3 L, 317.3 L, 357.7 L. Circumferential crack 360.9 L. Deposit/encrustation throughout L. | 1970 | 54
466 | ZUNI ST | M-3 | Z-16 |  | Z-15 | 291 | 289.6 | 10 | PVC | 3% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG1 | NO COMMENTS | 1970 | 54
467 | W 57TH AVE | M-3 | STUB |  | Z-15A | 3 | 3 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0 | 0 | REG1 | NO COMMENTS | -
468 | W 57TH AVE | M-3 | Z-15A |  | Z-15 | 242 | 242.3 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0 | 0 | REG1 | NO COMMENTS | 1970 | 54
469 | ZUNI ST | M-3 | Z-15 |  | Z-14 | 269 | 266.7 | 10 | PVC | 1.88% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | REG1 | NO COMMENTS | 1970 | 54
470 | W 58TH AVE | M-3 | STUB |  | Z-14A | 5 | 5 | 8 | VCP | 0.6% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG1 | UPSTREAM: Capped with bricks | -
471 | W 58TH AVE | M-3 | Z-14A |  | Z-14 | 264 | 268.1 | 8 | VCP | 0.6% | 2022 | - | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 7 | 4 | 0 | 25 | REG1 | UPSTREAM: Roots in joint @ 36 M, 41 M, 46 M, 51 M, 56 M, 61 M, 67 M, 71 M, 77 M, 81 L, 87 M, 92 L, 97 M, 99 M, 101 L, 106 L, 116 L, 121 L, 126 M, 142 M, 147 L, 152 L, 159 L, 179 L, 184 L, 194 L | 1970 | 54
472 | ZUNI ST | M-3 | Z-14 |  | Z-13 | 260 | 257.2 | 10 | PVC | 0.52% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG1 | NO COMMENTS | 1970 | 54
473 | W 59TH AVE | M-3 | Z-12 |  | Z-13 | 333 | 330.7 | 8 | PVC | 0.52% | 2018 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG1 | UPSTREAM: NO COMMENTS | -
474 | EASEMENT | M-4 | Z-13 |  | BE-01 | 126 | 125.6 | 10 | PVC | 3.36% | 2023 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 1 | 0 | 0 | 10 | REG1 | Deposits/grease attached through out L. | -
475 | ZUNI CT | M-4 | BE-07 |  | BE-06 | 347 | 347.1 | 8 | PVC | 2.41% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
476 | ZUNI CT | M-4 | BE-06 |  | BE-05 | 348 | 347.5 | 8 | PVC | 1.14% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
477 | ZUNI CT | M-4 | BE-05 |  | BE-04 | 377 | 376.5 | 8 | PVC | 1.13% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
478 | EASEMENT | M-4 | BE-04 |  | BE-03 | 154 | 152.9 | 8 | PVC | 1.55% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
479 | EASEMENT | M-4 | BE-03 |  | BE-02 | 136 | 136 | 8 | PVC | 3.85% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
480 | EASEMENT | M-4 | BE-02 |  | BE-01 | 67 | 66.2 | 8 | PVC | 2.78% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
481 | EASEMENT | M-4 | BE-01 |  | A-1H | 65 | 64.6 | 12 | PVC | 3.36% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
482 | ALCOTT ST | M-4 | A-1A |  | A-1B | 441 | 439.5 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 8 | 0 | 0 | 10 | REG1 | UPSTREAM: Some deposits attached L. | -
483 | ALCOTT ST | M-4 | A-1B |  | A-1C | 446 | 445.4 | 8 | PVC | - | 2022 | - | 20 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 16 | 0 | 0 | 40 | REG1 | Possible sag @ 50.4-54.3 L, tap 194.2 @ 2 (break-in) possible infil on bottom L. Some deposits attached L. | -
484 | ALCOTT ST | M-4 | A-1C |  | A-1D | 266 | 265.9 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 7 | 0 | 0 | 10 | REG1 | Some deposits attached L. | -
485 | EASEMENT | M-4 | A-1D |  | A-1E | 244 | 180.9 | 8 | PVC | - | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | -
486 | EASEMENT | M-4 | A-1E |  | A-1F | 160 | 158.4 | 12 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS | -
487 | EASEMENT | M-4 | A-1F |  | A-1G | 338 | 344.9 | 12 | PVC | - | 2023 | 5-15% | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | UPSTREAM; Sag: 0-25 M. | -
488 | EASEMENT | M-4 | A-1G |  | A-1H | 22 | 22.8 | 12 | PVC | - | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS | -
489 | W 59TH PL | M-3 | A1-H |  | Z-10 | 276 | 275.5 | 15 | PVC | - | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | -
490 | EASEMENT | M-3 | Z-12 |  | Z-11 | 188 | 188.2 | 8 | VCP | 1% | 2023 | 10-20% | 0 | 0 | 0 | 10 | 40 | 10 | 0 | 0 | 1 | 1 | 0 | 60 | RC1 | Point Repair: PVC 0-5.1. Roots 22.3 L, 52.4 L, 72.9 L, 117.8 L, 142 L, 153.1 L, 163.3 L, 166.9 L, 168 L . Sag 60-74 M, 90-147 M, 162-187 E. Deposits/encrustation thorughout L. Point Repair: PVC 184.1-187.4. | 1970 | 54
491 | EASEMENT | M-3 | Z-11 |  | PLP-02 | 13 | 13.1 | 12 | PVC | 5% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | Inside drop 9.1 | 2020 | 4
492 | EASEMENT | M-3 | PLP-17 |  | PLP-16 | 268 | 268.2 | 8 | PVC | 3.7% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
493 | EASEMENT | M-3 | PLP-16 |  | PLP-11 | 226 | 225.7 | 8 | PVC | 3.24% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
494 | EASEMENT | M-3 | PLP-15 |  | PLP-14 | 266 | 266.4 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
495 | EASEMENT | M-3 | PLP-14 |  | PLP-13 | 270 | 270.1 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
496 | EASEMENT | M-3 | PLP-13 |  | PLP-12 | 155 | 155.3 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
497 | EASEMENT | M-3 | PLP-12 |  | PLP-11 | 321 | 321 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
498 | EASEMENT | M-3 | PLP-11 |  | PLP-10 | 317 | 317.3 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
499 | EASEMENT | M-3 | PLP-10 |  | PLP-09 | 333 | 333 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
500 | EASEMENT | M-3 | PLP-09 |  | PLP-08 | 268 | 267.9 | 10 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG1 | UPSTREAM: Lot of grit at the end (upstream MH) L | 2020 | 4
501 | EASEMENT | M-3 | PLP-08 |  | PLP-07 | 250 | 250 | 10 | PVC | 0.4% | 2022 | - | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | Infil: runner L (right at the invert for the downstream MH 248.5) | 2020 | 4
502 | EASEMENT | M-3 | PLP-07 |  | PLP-06 | 15 | 14.5 | 10 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | UPSTREAM: NO COMMENTS | 2020 | 4
503 | EASEMENT | M-3 | PLP-06 |  | PLP-05 | 249 | 248.8 | 10 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
504 | EASEMENT | M-3 | PLP-05 |  | PLP-04 | 128 | 127.5 | 10 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
505 | EASEMENT | M-3 | PLP-04 |  | PLP-03 | 170 | 170 | 10 | PVC | 0.4% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NEW LINE | 2020 | 4
506 | EASEMENT | M-3 | PLP-03 |  | PLP-02 | 178 | 178 | 10 | PVC | 0.4% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NEW LINE | 2020 | 4
507 | EASEMENT | M-3 | PLP-02 |  | PLP-01 | 80 | 80 | 12 | PVC | 0.4% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NEW LINE | 2020 | 4
508 | EASEMENT | M-3 | PLP-01 |  | Z-10 | 77 | 77 | 12 | PVC | 0.4% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NEW LINE | 2020 | 4
509 | EASEMENT | M-3 | Z-10 |  | Z-9 | 130 | 137.1 | 15 | PVC | 8.08% | 2023 | 10% | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | MH Z-9 HAS ROOTS L. Deposits/encrustation throughout pipe L. | -
510 | EASEMENT | M-3 | Z-9 |  | Z-8 | 200 | 194.7 | 15 | DIP | 1.08% | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | 190-195 MATERIAL CHANGE TO PVC. | 2016 | 8
511 | EASEMENT | M-3 | Z-8 |  | Z-7-2 | 55 | 54.8 | 18 | PVC | - | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | OUTSIDE DROP 48.8’ | 2016 | 8
512 | EASEMENT | M-3 | Z-7-2 |  | Z-7-1 | 208 | 207.5 | 18 | PVC | - | 2023 | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2016 | 8
513 | EASEMENT | M-3 | Z-7-1 |  | Z-7 | 155 | 154.7 | 18 | PVC | - | 2023 | 15% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2016 | 8
514 | EASEMENT | M-3 | Z-7 |  | Z-6-1 | 102 | 104 | 18 | PVC | - | 2023 | 15% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2016 | 8
515 | EASEMENT | M-3 | Z-6-1 |  | Z-6 | 215 | 213.3 | 18 | PVC | - | 2018 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | REG1 | Possible sag @ 189-210 L | 2016 | 8
516 | Easement | M-4 | Z-6 |  | Z-5 | 232 | 231.4 | 15 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 40 | 20 | 0 | 0 | 0 | 0 | 0 | 60 | REG1 | Grease stuck @ top 0-8 E, 40-42 L, 56-68 M. Sag @ 13-117 E, 119-151 E. 25% capacity from 151 to end | 2016 | 8
517 | W 60TH AVE | M-4 | Z-5H |  | Z-5G | 280 | 280 | 8 | PVC | - | 2022 | - | 0 | 0 | 10 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 30 | REG1 | Egging/deformed joint @ 179 L, 193 L, 207 L, 235 L, 249 L. Sag @ 29-50 L, 73-82 L, 115-124 L, 197-226 L, 232-255 L, 268-276 L. Grit in the line L | 2016 | 8
518 | W 60TH AVE | M-4 | Z-5G |  | Z-5F | 286 | 285.7 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | Sag @ 16-23 L, 195-203 L, 274-283 L. Some grit & rock in the line L | 2016 | 8
519 | W 60TH AVE | M-4 | Z-5F |  | Z-5E | 191 | 190.5 | 8 | PVC | - | 2022 | - | 0 | 0 | 10 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 30 | REG1 | Sag @ 3-31 L. Egging/deformed joint @ 63 L. Some grit & rock in the line L | 2016 | 8
520 | W 60TH AVE | M-4 | Z-5E |  | Z-5D | 366 | 365.5 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG1 | Some grit & rock in the line L. Fragments of PVC in line; see no breaks in this line. | 2016 | 8
521 | W 60TH AVE | N-4 | Z-5D |  | Z-5C | 401 | 401.1 | 8 | PVC | - | 2022 | - | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | Egging/deformed joint @ 163 L. Some grit & rock in the line L | 2016 | 8
522 | W 60TH AVE | N-4 | Z-5C |  | Z-5B | 401 | 401 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG1 | Grit in the line L | 2016 | 8
523 | W 60TH AVE | N-4 | Z-5B |  | Z-5A | 350 | 350.1 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | Lots of grit; some rock in the line M | 2016 | 8
524 | W 60TH AVE | N-3 | Z-5A |  | Z-5 | 49 | 49.3 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | Lots of grit; some rock in the line M | 2016 | 8
525 | EASEMENT | N-3 | Z-5 |  | Z-4 | 244 | 242.8 | 18 | PVC | 0.35% | 2018 | - | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | NO COMMENTS; MH Z-4 looks like it has a grease build up all over the inverts and up the bench M | 1970 | 54
526 | EASEMENT | N-3 | Z-4 |  | Z-3 | 304 | 303.3 | 18 | PVC | 0.3% | 2018 | - | 20 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | REG1 | Point repair: liner 53.1; looks like an infil stain next to joint L. Egging/out of round through out pipe L. | 1970 | 54
527 | EASEMENT | N-3 | Z-3 |  | Z-2 | 281 | 280.8 | 18 | PVC | 0.3% | 2018 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 1970 | 54
528 | EASEMENT | N-3 | Z-2 |  | Z-1 | 312 | 308.1 | 18 | PVC | 0.3% | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 1970 | 54
529 | EASEMENT | N-3 | Z-1 |  | Z (meter station) | 160 | 154.1 | 15 | DIP | 0.3% | 2023 | 15-60% | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | REG1 | SAG: 41-88 E | 1970 | 54
[5 empty] | Totals- | 103262.58 | 102351.37 |  |  | Average |  |  | 25.1562 | 22.7273 | 14.0659 | 12.377 | 14.8718 | 12.3846 | 11.0989 | 11.039 | 1283 | 104 | 0 | 18.3081
[5 empty] | Number of lines | 529 | [6 empty] | 64 | 11 | 91 | 61 | 156 | 130 | 91 | 77
[5 empty] | Lines Done | 521

## Print-Legal
Overall System Condition Spreadsheet- BWSD
| ABBREVIATION KEY |  |  | CONDITIONS KEY | [20 empty] | Annual Maintenance Action
| CIP- CURED IN PLACE |  |  |  |  | INFILTRATION |  | BROKEN | JOINTS | ROOTS | SAGS | DEBRIS | CRACKS | DETERIORATION | [6 empty] | Lines Complete | Percentage | Linear Feet
| CI- CAST IRON |  |  | NONE |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 521 | 98.49% | 102351.37
| CO - CONCRETE |  |  | LIGHT |  | 20 |  | 20 | 10 | 10 | 10 | 10 | 10 | 10 | [10 empty] | H1- HOT SPOT: ANNUAL VIDEO/JET
| DI- DUCTILE IRON |  |  | MODERATE |  | 50 |  | 50 | 25 | 25 | 20 | 20 | 20 | 20 | [5 empty] | Still Needs Assessed |  | Percentage | Linear Feet |  | H2- HOT SPOT: VIDEO/JET EVERY 6 MONTHS
| P.E. - POLYETHYLENE |  |  | EXTENSIVE |  | 100 |  | 100 | 50 | 50 | 40 | 40 | 40 | 30 | [5 empty] | 8 |  | 1.512% | 911.21 |  | H/RC- HOT SPOT/ROOT CUT: VIDEO/JET EVERY YEAR//ROOT CUT EVERY 3 YEARS
| PVC - PLASTIC | [23 empty] | H/RC (H/RC1= YEAR 1 ROOT CUT, H/RC2= YEAR 2 ROOT CUT, H/RC3= YEAR 3 ROOT CUT)
| RL- RIB-LOC |  |  | EMERGENCY RANK: |  | 151+ | 1-REPAIR IMMEDIATELY |  |  | 100-150 |  | 2- REPAIR NEEDED/MONITOR ANNUALLY | [12 empty] | RC: ROOT CUT
| SL- SLIP-LINE | [19 empty] | PERCENTAGE |  | LINEAR FEET |  | RC (RC1= YEAR 1 ROOT CUT, RC2= YEAR 2 ROOT CUT, RC3= YEAR 3 ROOT CUT)
| ST- STUB/NO UPSTREAM ACCESS |  |  | SCORE: |  |  | 0-25 | OVERALL GOOD CONDITION | [6 empty] | CATEGORY 1 |  | GREEN |  |  |  | 63% |  | 64482.27 |  | REG: JET/VIDEO EVERY 3 YEARS
| VCP - CLAY | [5 empty] | 26-50 | OVERALL FAIR CONDITION | [6 empty] | CATEGORY 2 |  | YELLOW |  |  |  | 25.54% |  | 26142.6 |  | REG (REG1= YEAR 1 , REG2= YEAR 2, REG3= YEAR 3)
[7 empty] | 51-75 | OVERALL MODERATE CONDITION | [6 empty] | CATEGORY 3 |  | BLUE |  |  |  | 8.006% |  | 8194
[7 empty] | 76-100 | REPAIRS SHOULD BE SCHEDULED | [6 empty] | CATEGORY 4 |  | PURPLE |  |  |  | 3.451% |  | 3532.5
[7 empty] | 101+ | EMERGENCY |  | (DEPENDING ON NOTES) |  |  |  |  | CATEGORY 5 |  | RED |  |  |  | 0% |  | 0
| STREET | MAP | MH | TO | MH | LENGTH | VIDEO FEET | SIZE | TYPE | SLOPE | LAST VIDEO | % FULL | INFILTRATION | BROKEN | JOINTS | ROOTS | SAGS | DEBRIS | CRACKS | DETERIORATION | TAPS | CAPPED TAPS | EMERGENCY RANK | OVERALL SCORE | MAINTENANCE ACTION | OPERATOR NOTES AND CAPITAL IMPROVEMENTS | YEAR INSTALLED | AGE
45 | EASEMENT | L-7 | S-12 |  | S-11 | 278 | 279.1 | 12 | VCP | 0.22% | 2023 | 10% | 50 | 0 | 10 | 0 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 100 | REG2 | 198’ INFILL RUNNER M. Sealing rings in a lot of joints look worn or are coming out of the joint L. Sags: 50-92 L, 154-261 L. Deposits/encrustation attached throughout pipe L. Deterioration? side of pipe looks rough 150.2 L. Crack at top of pipe near joint 183.4 L, 203.3 L, circumferential crack 275 L. | 1973 | 51
102 | EASEMENT | L-6 | Q-2 |  | Q-1B | 65 | 66.5 | 8 | DIP | 75.2% | 2023 | 5-20% | 0 | 0 | 0 | 50 | 0 | 20 | 20 | 10 | 0 | 0 | 0 | 100 | REG2 | CORROSION THROUGHOUT L, Multiple fractures M and Mass of roots 52.2 E, 64.5 ENCRUSTATION M | 1976 | 48
105 | EASEMENT | L-6 | Q-1A |  | P-1 | 130 | 127.7 | 8 | VCP | 0.4% | 2023 | 5% | 50 | 0 | 10 | 0 | 20 | 10 | 0 | 10 | 0 | 0 | 0 | 100 | REG2 | 7.5 ENCRUSTATION throughout L , 112.5 INFILL RUNNER IN JOINT M, POINT REPAIR: PVC 121.8-125 w/offset joint L. Sag 98-122 M. Pitting/deterioration 2 L, crack at to pof piep near joint 96.4 L, infil in joint at point repair RUNNER 121.8 M. | 1976 | 48
113 | EASEMENT | L-6 | P-1 |  | O-1 | 224 | 225.9 | 8 | VCP | 0.4% | 2023 | 5-15% | 50 | 0 | 0 | 0 | 10 | 20 | 10 | 10 | 0 | 0 | 0 | 100 | REG2 | POINT REPAIR: PVC 0-3.8, 19.4 CRACK MULTI L, 58 ENCRUSTATION M, 84 INFILL DRIPPER/Runner M, 211.5 ENCRUSTATION, 218.6 ENCRUSTATION M. Possible infil around invert connection in MH P-1 L. Sags/high spots throughout 31-225 end L. Deterioration/pitting throughout M. Possible infil stain in joint/seperations? 38.9 L. Possible crack 2 side mid pipe L. Deposits/encrustation throughout L except: 6.3 M, 24 M, 29 M, 44.1 M, 62 M, 76.2 M, 94.9 M. | 1976 | 48
37 | W 54TH AVE | L-7 | S-12F-2 |  | S-12F-1 | 112 | 111.5 | 8 | CIP | 0.4% | 2023 | 15% | 50 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | REG2 | Infil: weeper 76.5 M. Sag: 27-52 L, 82-102 E. | 1976 | 48
77 | TENNYSON ST | L-7 | TN-4 |  | TN-3 | 402 | 403.1 | 8 | VCP | 1% | 2023 | 10-15% | 50 | 0 | 0 | 0 | 20 | 10 | 10 | 0 | 3 | 0 | 0 | 90 | RC2 | ENCRUSTATION 61.2 L, 169.3 INFILL GUSHER M, 189.1 CRACK LONG L, ENCRUSTATION 236.8 L, SAG 312-321 M, 329-340 M. Crack 24 L, 29 L, 94 L, 110 L, 115 L, 120 L, 122 L, 150 L. Sag: 115-124 L, 128-135 L, 295-300 L. | 1974 | 50
183 | W 53RD AVE | L-5 | STUB:I-3A |  | I-3 | 122.5 | 124.8 | 8 | VCP | - | 2023 | 5% | 20 | 0 | 0 | 10 | 10 | 10 | 20 | 20 | 4 | 1 | 0 | 90 | H/RC3 | 3 Roots Fine Joint L , 27.6 Crack Longitudinal L, 68.6 Crack Longitudinal L, sag 78.5-85 L, 88.4 Crack Longitudinal L w/infil stain L, longitudinal crack in the bottom of pipe 105.7-109 L, sags 108-115, 122-129 L, 131.2 Crack Multiple L, 191.6 Crack Circumferential L, 200.4 Crack Circumferential L, 201.9 Crack Longitudinal L, 203.2-214.4 multiple Cracks M, 214.4 Roots . Debris/encrustation throughout L, pitting/deterioration throughout L-M. | -
406 | W 53RD AVE | L-3 | T-8E |  | T-8D | 300 | 298.2 | 8 | VCP | 2.8% | 2021 | - | 20 | 0 | 25 | 10 | 0 | 10 | 10 | 10 | 8 | 0 | 0 | 85 | RC1 | UPSTREAM: Joints offset throughout: 1 L, 8 L, 14 L, 23 L, 39 L, 44 L, 49 L, 59 M, 68 L, 74 M, 79 L, 84 L, 94 L, 99 L, 104 L, 109 L, 119 L, 124 L, 129 M, 134 L, 139 M, 149 L, 154 M, 159 L, 169 L, 171 L, 179 M, 184 L, 189 L, 199 L, 204 M, 214 L, 219 L, 224 M, 229 L, 234 L, 249 L, 255 M, 260 L, 270 M, 280 M, 285 L, 290 L. Roots in joints @ 24 L, 44 L, 49 L, 59 L, 74 L, 79 L, 89 L, 99 L, 104 L, 109 L, 119 L, 129 L, 139 L, 154 L, 159 L, 185 L, 189 L, 194 L, 199 M, 205 L, 209 L, 214 L, 229 L, 249 L, 254 L, 264 L, 269 L, 274 L, 284 L, 299 L. Deterioration @ 164 L in joint. Deposits attached through out L. Possible circumferential crack @ 156 L, 167 L, 212 L, 246 L, 282 L. Possible infil in joint @ 34 L, 44 L, 49 L, 64 L, 69 L, 94 L, 99 L, 104 L, 109 L, 124 L, 129 L, 134 L, 154 L, 174 L, 184 L, 199 L, 214 L, 224 L. | 1978 | 46
44 | EASEMENT | L-7 | S-12A |  | S-12 | 249 | 248.5 | 12 | VCP | 0.33% | 2023 | 10% | 50 | 0 | 10 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 80 | REG2 | CRACK L W/INFILL 2.3RUNNER M, Point repair: PVC 24-39.5, EVERY JOINT IS CRACKED GOOD PIPE FOR LINNING. Sags throughout L. Crack at the top of pipe near joint 79L, 212.1 L | -
130 | NEWTON ST | L-6 | N-3 |  | N-2 | 300 | 291.9 | 8 | VCP | 2.68% | 2023 | 5% | 20 | 20 | 0 | 0 | 0 | 20 | 10 | 10 | 8 | 0 | 0 | 80 | REG2 | 1 Deposits/encrustation M & circumferential crack L possible infil L, circumferential crack at tap 20 L, point repair: PVC 174.9 w/offset & seperation L, 175.7 broken pipe infil/exfiltration L, 29 pitting/deterioration L, 54 pitting/deterioration L, 64.4 Cracked pipe w/possible infill L, 78 crack w/ possible infill L, spiral fracture at joint 159 M, 286.5 circumferential crack L. Deposits/encrustation throughout pipe L. | -
251 | EASEMENT | L-5 | BE-57A |  | BE-57 | 210 | 213.3 | 10 | P.E. | 0.2% | 2021 | - | 0 | 20 | 0 | 0 | 40 | 20 | 0 | 0 | 2 | 0 | 0 | 80 | H1 | Sags throughout starting @ approx. 89-130, 132-150, & 185-213 5%-50%+ E. Deposits/encrustation throughout: grease, grease glob at top of pipe approx 138.8 M. Looks like hole/break through at approx. 189.7 (blue rag?) 2 side L. | -
356 | W 55TH AVE | L-4 | BR-6 |  | B-1C | 301.6 | 161.4 | 8 | VCP | 0.4% | 2023 | 5-15% | 20 | 0 | 0 | 10 | 20 | 20 | 10 | 0 | 4 | 0 | 0 | 80 | H/RC3 | 5.9 Infiltration: Dripper Connection L/deposits/encrustation M, joint @ 6.6 appears to also have deposits/encrustation M & possible infiltration stain L, 7.4 Multiple Cracks with deposits/encrustation M & possible infil stain L, 56.7 Deposits Attached Encrustation M, tap 78 has Roots Ball Lateral E. Sag from 140-161 M. 144.3 circumferential crack L. Deposits/encrustation throughout L | 1976 | 48
392 | ZUNI ST | L-3 | Z-23 |  | Z-22 | 326 | 322.5 | 8 | VCP | 5.08% | 2022 | - | 20 | 20 | 10 | 10 | 0 | 0 | 10 | 10 | 7 | 0 | 0 | 80 | RC1 | Point repair 175-180: offset @ 175 L. Possible infil in joint @ 1 L, 61 L, 66 L, 82 L, 94 L, 175 L, 189 L, 211 L, 235 L, 260 L, 280 L, 296 L, 306 L. Egging/deformed around tap 177.3 L. Roots in joint @ 81 L, 87 L, 133 L, 139 L, 142 L, 148 L, 168 L, 173 L, 183 L, 188 L, 194 L, 199 L, 204 L, 209 L, 214 L, 219 L, 224 L, 229 L, 234 L. Crack in joint 132 L, broken/missing piece @ top of joint 194 L. Possible candidate for lining | 1973 | 51
422 | W 54TH AVE | L-3 | W-4 |  | V-10 | 362 | 357.5 | 8 | VCP | 0.56% | 2022 | - | 0 | 20 | 10 | 0 | 20 | 20 | 10 | 0 | 6 | 1 | 0 | 80 | REG1 | Deposits/encrustation at beginning of pipe M, aroung tap @ 54.9 M, deposits/encrustation through out rest of pipe L. Sag @ 17-24 L, 49-60 L, 79-90 L, 93-106 L, 111-115 L, 119-141 L, 160-185 M, 190-200 L, 211-216 L, 233-256 M, 276-285 M, 291-296 L, 308-332 M, 349-355 L. Off set joint @ 119 L, 155 L, 210 L, 225 L, 235 L, 270 L, 280 L, 285 L, 350 L. Broken 291.4 @ 2 L. Circumferential Crack 353.7 L. | 1972 | 52
463 | W 59TH PL | M-3 | V-1 |  | Z-12 | 303 | 300.6 | 8 | VCP | 0.4% | 2021 | - | 20 | 20 | 10 | 10 | 10 | 10 | 0 | 0 | 9 | 0 | 0 | 80 | RC1 | Point repair: PVC 0-15 Material change: PVC @ 295. Joint separated or broken @ 15 L w/possible infil L. Joint offset @ 17 L, 47 L, 103 L, 266 L, 271 L. Roots in joint @ 22 L, 27 L, 37 L, 73 L, 82 L, 87 L, 93 L, 98 L, 108 L, 113 L, 123 L, 128 L, 133 L, 145 L, 155 L, 160 L, 165 L, 170 L, 256 L, 283 L. Possible Sag @ 70-78 L, 108-127 L, 160-182 L, 265-296 M. Deposits/encrustation throughout L. Invert in Z-12 Diverted North for some reason; CIP- Remove diversion to flow through to Z-13 & abandon Z-12 -PLP-02 as well as vacate easement if possible. | 1970 | 54
30 | EASEMENT | L-8 | S-12L |  | S-12K | 56 | 58 | 10 | VCP | 0.3% | 2023 | 5-10% | 20 | 0 | 25 | 0 | 10 | 10 | 10 | 0 | 0 | 0 | 0 | 75 | REG2 | UPSTREAM: AT 5.3 IN COULD NOT PASS OFF SET. DOWNSTREAM VIDEO; ABANDON VIDEO AT 51’ OFFSET M. Sealing ring in the beginning of pipe/obstruction but they were able to get around it. Crack with infil stain at top of pipe 2.5 L, joint with infil stain/deposits L & crack L, infil stain at point repair 51.7 L. Sag 9-33 L. Point repair: PVC 51.7- end MH | -
432 | UMATILLA ST | L-3 | U-6 |  | U-5 | 254 | 106.8 | 8 | RL | 4.36% | 2018 | - | 0 | 50 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 75 | REG1 | Damage at the top of the pipe 35.9 M. ABANDONED; UNABLE TO PASS DAMAGE. UPSTREAM; Pipe out of round 70.9 M. ABANDONED; UNABLE TO PASS. | -
12 | RALSTON FRONTAGE RD | M-8 | S-22B |  | S-22A | 246 | 245.9 | 8 | VCP | - | 2023 | 5% | 50 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 3 | 0 | 0 | 70 | REG2 | Sag through out 23-154 L. Deposits/encrustation throughout L. Infil: runner in joint 94.4 M, 104.7 L. Infil stain 28.5 L. | -
28 | EASEMENT | L-8 | S-12N |  | S-12M | 267 | 265.7 | 10 | VCP | 0.3% | 2023 | 10% | 50 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 70 | REG2 | 248.1 CRACK LONG W/INFILL WEEPER L, 251.1 CRACK MULTIPLE M & INFILL WEEPER/Runner L, 256.1 FRACTURE LONGITUDE M, 260.5 INFILL WEEPER L, 262.6 CRACK MULT M, INFILL THROUGH OUT PIPE. | -
72 | ST CLAIR PL | L-7 | TN-8A |  | TN-8 | 258 | 255.8 | 8 | VCP | 0.4% | 2023 | 5-15% | 0 | 20 | 0 | 10 | 20 | 0 | 10 | 10 | 0 | 0 | 0 | 70 | RC2 | CRACK 2 CIRC L, 4.6 Break W/ROOTS L, ENCRUSTATION 62-79, 204.2 ROOTS IN JOINT L, SAG 229-255.8 M. Roots in joint: 71.6 L. Sag: 13.8-21 L, 25-52 L, 56-72 L, 94-102 L, 127-153 L, 188-199 L, 218-225 L. Buldge in side of pipe w/crack 163.1 L, 165.8 L | -
79 | TENNYSON ST | L-6 | TN-2 |  | S-8 | 401 | 401.7 | 15 | VCP | 0.4% | 2023 | 10% | 20 | 0 | 10 | 0 | 20 | 10 | 10 | 0 | 2 | 0 | 0 | 70 | REG2 | 244.3’ INFILL RUNNER L in joint sealing ring deterioration L. Infil stain at joint 43 L, 52.7. Deteriorated/cracked joint w/infil stain 229.3 L, 343.7 L. Infil stain at top of pipe 2 Side: possible crack or hole 394.6 L. Deposits/encrustation throughout L. Sags: 15-47 L, 104-120 L, 156-167 L, 193-232 M, 240-253 L, 258-288 L, 312-395 M. | 1973 | 51
124 | EASEMENT | L-6 | S-4 |  | S-3 | 257 | 230.5 | 15 | VCP | 0.22% | 2023 | 5-15% | 20 | 0 | 0 | 0 | 20 | 10 | 20 | 0 | 0 | 0 | 0 | 70 | REG2 | Spiral Fracture M (167.2-173.1) w/INFILL 167.2 L. Deposits/encrustation throughout L. Sag: 17-118 L, 130-213 M | 1974 | 50
125 | EASEMENT | L-6 | S-3 |  | S-2 | 300 | 300.7 | 15 | VCP | 0.22% | 2023 | 10-20% | 20 | 20 | 0 | 0 | 20 | 0 | 10 | 0 | 0 | 0 | 0 | 70 | RC2 | BROKEN PIPE AT TOP 114.4 L. Sags: 8-53 M, 81-200 M, 204-278 M. Possible infil in bottom/sides on joint 70.9 L, 77.9 L, 283.3 L. Circumferential crack 257.8 L, 294 L. | 1973 | 51
196 | JULIAN ST | L-5 | J-4 |  | J-3 | 164 | 162 | 8 | VCP | 1.48% | 2017 | - | 20 | 0 | 0 | 10 | 10 | 10 | 10 | 10 | 2 | 0 | 0 | 70 | RC3 | Roots in joint: 56.6 L, 61.6 L, 66.3 L, 139.3 L. Sags: 15-23 L, 80-87 L. Deterioration/pitting & debris throughout L. Crack near joint 119.8 L, fracture at joint 134.8 L, circumferential crack 157.5 L. Possible Infil in joint 149.3 L. | 1976 | 48
244 | EASEMENT | L-5 | L-4F1 |  | L-4F | 159 | 158.2 | 8 | VCP | 4.52% | 2019 | - | 50 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 70 | REG3 | Multiple circumferential crack 7.2 L (root cut saw), looks like multiple circumferential cracks w/encrustation or possible infil 40.3-46.0 L, circumferential crack w/infil runner 156.2 M | 1977 | 47
274 | W 56TH AVE | M-4 | BE-52A |  | BE-52 | 118 | 115.8 | 10 | P.E. | - | 2021 | - | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 20 | 2 | 0 | 0 | 70 | REG3 | Sag 47-69 E. Failing sealing ring @ 69 E. Note says: 3 BUCKETS OF DEBRIS REMOVED FROM LINE | -
455 | WYANDOT ST | M-3 | W-3 |  | W-2 | 345 | 347.5 | 8 | VCP | 0.95% | 2023 | 5-15% | 20 | 0 | 0 | 10 | 20 | 0 | 10 | 10 | 4 | 0 | 0 | 70 | H/RC1 | Point repair: PVC 0-5. Roots in joint: 62.2 L, 73.1 L, 78.5 L, 110.3 L, 115.5 L, 142.3 L, 340.5 L. Sag: 30-53 M, 68-79 L, 86-95 L, 137-145 L, 288-315 M. Surface damage/deterioration 5-21 L. Crack top of pipe near joint 151.9 L, 318.9 L. Possible infil in joint 19.6 L, 169.5 L. Point repair: PVC 265.1-273.7. | -
94 | EASEMENT | L-6 | R-2 |  | R-1 | 174 | 176.1 | 8 | VCP | 4.96% | 2023 | 5% | 20 | 0 | 0 | 25 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 65 | RC2 | UPSTREAM: 7.4 DEPOSITS/ENCRUSTATION M, 8.7 INFILL DRIPPER L, 30.6 ROOTS IN JOINT L, 46.6 ROOTS IN JOINT M, 71.7 ROOTS IN JOINT L, 87.3 ROOTS IN JOINT M, 97.6 ROOTS IN JOINT L, 143.9 ROOTS IN JOINT L, 162.9 ROOTS IN JOINT L, NEEDS ROOT CUT THEN LINED. Roots in joint: 61.8 L, 92.3 L, 107.3 L, 122.6 L, 127.7 L, 132.7 L. | 1976 | 48
420 | WYANDOT ST | L-3 | W-5 |  | W-4 | 341 | 337.1 | 8 | VCP | 5.64% | 2022 | - | 20 | 0 | 10 | 25 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 65 | RC1 | Roots in joint @ 181M, 191 M, 199 L, 223 L, 233 M, 239 M, 241 M, 289 L; All cut. Possible infil in the joint @ 13 L, 18 L, 23 L, 28 L, 53 L, 73 L, 78 L, 83 L, 118 L. Joints offset @ 28 L, 58 L, 68 L, 128 L, 148 L, 153 L, 158 L, 168 L, 173 L, 178 L, 183 L, 188 L, 193 L, 208 L, 213 L, 223 L, 248 L, 283 L, 313 L, 323 L. Possible circumferential crack @ 74 L, 105 L. | -
426 | VALLEJO ST | L-3 | V-10 |  | V-9 | 338 | 334.3 | 8 | VCP | 5.1% | 2022 | - | 20 | 0 | 25 | 10 | 0 | 0 | 10 | 0 | 7 | 0 | 0 | 65 | REG1 | Joint offset @ 2.2 M, 5 M, 35 L, 45 L, 50 L, 60 L, 75 L, 86 L, 127 L, 157 L, 172 L, 182 L, 207 L, 222 L, 227 L, 232L, 253 M, 298 M. Crack @ joint 2.2 L, around tap 244 L, @ joint 192, 323, & 328 L. Possible infil in joint @ 35 L, 45 L, 50 L, 60 L, 75 L, 86 L, 112 L, 122 L, 127 L, 152 L, 157 L, 162 L, 167 L, 172 L, 182 L, 192 L, 207 L, 222 L, 227 L, 232 L, 253 L, 278 L, 293 L, 298 L, 303 L, 323 L. Liner; point repair @ 265-269. Roots in joints @ 102 L, 107 L, 162 L, 283 L, 328 L. Possible candidate for lining. | -
9 | EASEMENT | M-8 | S-24 |  | S-23 | 48 | 45 | 8 | VCP | 0.4% | 2023 | 5% | 20 | 0 | 0 | 0 | 10 | 20 | 10 | 0 | 0 | 0 | 0 | 60 | REG2 | OUTSIDE DROP 41.5. Lot of grit in line M, possible sag 0-16 L, possible crack with infill on other side of drop L, possible infil in drop at joint L. | 1982 | 42
11 | RALSTON FRONTAGE RD | M-8 | S-22C |  | S-22B | 74 | 71.4 | 8 | VCP | - | 2023 | - | 20 | 0 | 0 | 0 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 60 | REG2 | 19.4 multiple fracture w/deposits and infil stain L, infil: dripper 26.6 L. Sag: 32-39 L, 50-59 L. Deterioration/pitting thorughout L. Infil stain around joint 42.4 L. Nothing upstream and no taps in line: Could probably be plugged or abandoned. | -
15 | EASEMENT | M-8 | S-21 |  | S-19 | 285 | 238.6 | 10 | DIP | 0.3% | 2023 | 5-20% | 20 | 0 | 0 | 0 | 20 | 10 | 0 | 10 | 0 | 0 | 0 | 60 | REG2 | SAG 92-127.5 M. Deposits/encrustation thorughout L, and deterioration L. Hard to tell but may have some infil stains at joints: 31.6 for example L. | -
70 | EASEMENT | L-7 | TN-8C |  | TN-8B | 240 | 237.5 | 8 | VCP | 0.4% | 2023 | 5% | 0 | 0 | 10 | 10 | 20 | 0 | 10 | 10 | 1 | 0 | 0 | 60 | RC2 | Roots in joint: 25.7 L, 35.9 L, 56 L, 61.2 L, 86.5 L, 96.6 L, 111.7 L, 137 L, 162 L, 187.6 L, 192.7 L, 207.9 L, 228.1 L. Broken Joint 51.1 L possibly seperated. Sag: 5-36 L, 50-56 L, 67-82 L, through out 94-235 L/M. Deterioration at joint 17.9 L, 30.2 L, 172.2 L. Pitting/deterioration 151.1 L. Buldge in pipe or crack at top 2 side 127 L, 129.5 L. Crack at top of pipe 218.1 L. | -
76 | TENNYSON ST | L-7 | TN-5 |  | TN-4 | 348 | 348.4 | 8 | VCP | 7% | 2023 | 5% | 20 | 0 | 0 | 10 | 0 | 10 | 10 | 10 | 2 | 0 | 0 | 60 | RC2 | ENCRUSTATION 0-65 L. Roots in joint: 288.9 L. Encrustation 336-346 L. Crack: 81.6 L, 106.3 L, 146.7 L, 161.8 L, 187 L, 196.5 L, 212.2 L, 226.7 L, circumferential 253.9 L, 271.6 L, 286.4 L, 297.2 L, 312 L. Pitting deterioration: 154.8 bottom 2 side of pipe L. Possible infil in joint: 132.7 L, 137.9 L, 198 L, 343.3 L. | 1974 | 50
78 | TENNYSON ST | L-7 | TN-3 |  | TN-2 | 395 | 394 | 8 | VCP | 0.52% | 2023 | 10-15% | 0 | 0 | 0 | 10 | 20 | 10 | 10 | 10 | 1 | 0 | 0 | 60 | REG2 | SAG 103-112.5 L,121.5-126.5 L, 131-140 M, 325-368 M, 380-391 L. Joint 267.6 PIECE OF PIPE ON TOP IS GONE L (no hole). Roots or debris in joints throughout/ eposits/encrustation thorugh out L, video is a little foggy/hard to tell L. Sag: 181-192 L, 231-242 L, 295-305 L. Possible crack 10 side 50 L, top of pipe 70 L, 10 side 90 L, 10 side 155 L, 10 side 180 L, 10 side 220 L, 10 side 260 w/buldge L, 10 side 306 L, 2 side 311 L, 2 side 321 L, 2 side 331 L, 2 side 361 L, Circumferential crack at tap 254 L. | 1974 | 50
123 | EASEMENT | L-6 | O-1 |  | S-4 | 424 | 426.6 | 8 | VCP | - | 2023 | 5% | 20 | 0 | 0 | 10 | 10 | 0 | 10 | 10 | 0 | 0 | 0 | 60 | H/RC2 | Roots in joint 41.7 L, 62.1 L, 68.2 L, 72.1 L, 189 L, 209.2 L,229.4 L, 234.6 L, 239.5 L, 249.6 L, 259.5 L, 274.7 L, 295 L, 299.7 L, 309.9 L, 319.8 L, 329.7 L, 339.8 L. Point repair: PVC 279-290. Something stuck in the bottom of joint 128.3: roots? Sags throughout pipe back to back L.Possible infil stain in joint 147.8 L. Crack in joint 219 L, 244.4 L, 379.8 L. Pitting/deterioration 272.4 top of pipe L. | 1974 | 50
140 | W 54TH AVE | L-6 | M-1 |  | L-8 | 286 | 285.1 | 8 | VCP | 1% | 2023 | 5-15% | 20 | 0 | 0 | 0 | 20 | 0 | 10 | 10 | 3 | 1 | 0 | 60 | REG2 | Infil at top of pipe 0 L (can't see where it's coming in), pitting/deterioration at joint 8.8 L, 49.4 L, 95 L, 211 L, crack at top of pipe 74.3 L, 226.8 L, crack in 2 side of pipe 100 L, crack in 10 side of pipe 130.1 L, crack in 2 side bottom 163.2L, crack 10 side 264 L, point repair: PVC 208.6-211 w/seperation at joint L. Sags throughout L except: 144-161 M, 183-192 M, 199-212 M, 253-268 M. | 1975 | 49
190 | JULIAN ST | L-5 | J-6 |  | J-5 | 399 | 385.6 | 8 | VCP | 2.94% | 2013 | - | 20 | 0 | 0 | 0 | 0 | 20 | 10 | 10 | 7 | 7 | 0 | 60 | RC3 | Spiral fracture 6.8 L, Point repair: PVC 9.4-13.1. Joint seperation at point repair 13.1 L with infil L, crack near joint/top 15.1 L, circumferential crack near joint 42.9 L, circumferential crack near joint 50.6 L, multiple fracture near joint 54.6 L, longitudinal fracture 63.7 L, circumferential fracture 81.9 L, circumferential crack near top of joint 125.9 L, longitudinal crack near top of pipe/joint 131.3 L, circumferential crack near joint top of pipe 149.1 L, offset joint 161.1 L. Deterioration/pitting throughout L, deposits attached throughout L except: 50.7 M, 105.2 M, 164 M, 189.9 M. Roots in joints thorughout L. ABANDONED: couldn't pass deposits at 189.9. UPSTREAM; Drop into MH J-5. Crack near joint top of pipe 13.8 L, point repair: PVC 18.9-21.7, encrustaiton/deposits attached 44.7 L, 157.0 M, 189.9 M, 195.7 M. ABANDONED; couldn't pass deposits. Sags throughout L. | -
198 | JULIAN ST | L-5 | J-2 |  | J-1 | 212 | 209.1 | 8 | VCP | 4% | 2017 | - | 20 | 0 | 0 | 0 | 10 | 0 | 10 | 20 | 3 | 0 | 0 | 60 | REG3 | UPSTREAM; Circumferential fracture 1.5 L, multiple circumferential cracks 7.1 L (root cut saw), deterioration 110.5-124.1 M, circumferential crack 205.3 L. Sag: 65-72 L. Point repair: PVC 128.7-133.1. Possible infil in bottom of joint: 39.6 L, 54.1 L, 59.4 L, 89.0 L, 152.2 L, 181.8 L, 201.0 L. | 1978 | 46
250 | EASEMENT | L-5 | L-4A |  | L-2 | 250 | 251.1 | 8 | CIP | 0.4% | 2020 | - | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 20 | 0 | 0 | 0 | 60 | REG3 | Sag: 16.5-35 M, 50-62 L, 102-194 M-E, 202-221 M. Damage to liner 241.8-247.8 L, delamination 247.8-250.6 M | 1977 | 47
412 | W 53RD AVE | L-3 | T-8B |  | T-8A | 323 | 323.8 | 8 | VCP | 2.48% | 2023 | 5% | 20 | 0 | 0 | 10 | 0 | 10 | 10 | 10 | 4 | 0 | 0 | 60 | RC1 | Roots 188.6 L, 198.6 L, 208.7 L. Circumferential crack 78.6 L, 203 L, 316.2 L, 318.3 L ;Root cut saw marks thorughout L. Deposits/encrustation throughout L. Possible infil in bottom of pipe 173.7 L, 178.8 L, 183.9 L, 233.5 L. | 1978 | 46
456 | W 56TH PL | M-3 | W-2A |  | W-2 | 285 | 307.9 | 8 | VCP | - | 2023 | 10% | 0 | 0 | 0 | 10 | 40 | 0 | 10 | 0 | 7 | 0 | 0 | 60 | H/RC1 | Roots 150 L, 164.4 L, 222.3 L. Sag 28-97 E, 105-132 M, 150-200 M, 220-250 E, 259-304 E. Crack on 10 side near joint 216.9 L. | -
490 | EASEMENT | M-3 | Z-12 |  | Z-11 | 188 | 188.2 | 8 | VCP | 1% | 2023 | 10-20% | 0 | 0 | 0 | 10 | 40 | 10 | 0 | 0 | 1 | 1 | 0 | 60 | RC1 | Point Repair: PVC 0-5.1. Roots 22.3 L, 52.4 L, 72.9 L, 117.8 L, 142 L, 153.1 L, 163.3 L, 166.9 L, 168 L . Sag 60-74 M, 90-147 M, 162-187 E. Deposits/encrustation thorughout L. Point Repair: PVC 184.1-187.4. | 1970 | 54
516 | Easement | M-4 | Z-6 |  | Z-5 | 232 | 231.4 | 15 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 40 | 20 | 0 | 0 | 0 | 0 | 0 | 60 | REG1 | Grease stuck @ top 0-8 E, 40-42 L, 56-68 M. Sag @ 13-117 E, 119-151 E. 25% capacity from 151 to end | 2016 | 8
21 | EASEMENT | L-7 | S-14 |  | S-13 | 346 | 345.1 | 12 | PVC | 0.2% | 2023 | 5-15% | 0 | 0 | 25 | 0 | 20 | 10 | 0 | 0 | 0 | 0 | 0 | 55 | REG2 | SAG 65-73 L, SAG 81-103 L, SAG 113-130 L, SAG 262-343 M. THERE IS A LOT OF GRIT/SAND THROUGH THE MAIN. Egging joints throughout L Except: 81.5 M, 93.3 M, 112.5 M, 131.7 M, 304.1 M. | -
152 | KING CT | L-5 | K-8 |  | K-7 | 173 | 173.1 | 8 | VCP | 4% | 2023 | 5-15% | 0 | 0 | 0 | 25 | 0 | 20 | 10 | 0 | 3 | 0 | 0 | 55 | RC2 | 4 Roots Fine Joint L, 50.2 Roots Fine Joint M, 67.9 Roots Fine Joint M, 79.5 Roots Fine Joint M, 98.9 Roots Fine Joint L, 103.6 Roots Fine Joint L, roots 108 L, 167.7 Deposits Settled Compacted M:Attempted root cut with little success, 169.7 Crack Circumferential L | 1971 | 53
189 | W 54TH AVE | L-5 | J-6A |  | J-6 | 236.5 | 236 | 8 | VCP | - | 2023 | 5% | 0 | 0 | 25 | 0 | 10 | 10 | 10 | 0 | 4 | 5 | 0 | 55 | H/RC3 | Sags 10.8-21.8L, 35.6-56 L, 143.4-177 L. Point repair:PVC offset 89.3-92.7 Joint Separated M, 183.9 Crack Longitudinal L, point repair: PVC 227.1-231.7 offset L seperated/broken joint 231.7 M. Deposits/ecrustation throughout L. | -
5 | SHERIDAN FRONTAGE RD | M-8 | S-28 |  | S-27 | 182 | 180.1 | 8 | PVC | - | 2023 | 5-10% | 20 | 0 | 10 | 0 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 50 | REG2 | Sag 153-170.5 M. Material change: VCP 170.5. Joint offset 169.8 L. Possible infil in tap L. | -
13 | RALSTON FRONTAGE RD | M-8 | S-22A |  | S-22 | 235 | 251.1 | 8 | VCP | - | 2023 | 5% | 20 | 0 | 0 | 0 | 10 | 10 | 0 | 10 | 2 | 0 | 0 | 50 | REG2 | Infil: Gusher in tap 8 E, possible infil gusher in tap 80.8 E, infil: weeper238.7 L. Sags throughout L, debris/encrustation throughout L, deterioration througout L. Longitudinal crack 87.5 L, Longitudinal crack 151.2 L w/ infil stain L. | -
14 | EASEMENT | M-8 | S-22 |  | S-21 | 240 | 273.7 | 10 | VCP | - | 2023 | 5% | 20 | 0 | 0 | 0 | 0 | 10 | 20 | 0 | 1 | 0 | 0 | 50 | REG2 | 58.7 ENCRUSTATION L, 71.1 INFILL STAIN L, 93.6 ENCRUSTATION L, 128 CRACK SPIRL GOES ALONG BOTTOM OF MAIN COULD BE EXFILLTRATION M, 159.8 ENCRUSTATION M, 196.6 CRACK CIRCUM L. Infil stain at joint 49 L, 178.3 L, 226.4 L, 261.2 L. | -
75 | TENNYSON ST | L-7 | TN-6 |  | TN-5 | 50 | 55.1 | 8 | VCP | 6.72% | 2023 | 5% | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 10 | 0 | 0 | 0 | 50 | REG2 | ENCRUSTATION 0-49.4 M. Point Repair: PVC 45.7-49.4. Possible infil bottom of joint: 9.2 L, 39.5 L. Deterioration in the drop at the joint L. | -
86 | RALEIGH ST | L-6 | R-5 |  | R-4 | 400 | 385.8 | 8 | VCP | 4.23% | 2023 | 5% | 0 | 0 | 10 | 10 | 0 | 10 | 10 | 10 | 15 | 10 | 0 | 50 | RC2 | Roots 360.2 L. Object wedged in the joint @ 148.3 passed with no problem, could be seal: was pushed back down. Offset joint 385 L. Circumferential crack 2.3 L, multiple circumferential cracks 362.9-366 L (from root cut saw?). Deterioration/pitting throughout L. | -
115 | OSCEOLA ST | L-6 | O-6 |  | O-5 | 351 | 349.1 | 8 | VCP | 4.32% | 2023 | 5% | 0 | 0 | 0 | 10 | 10 | 0 | 20 | 10 | 9 | 0 | 0 | 50 | RC2 | Roots in joint 158.3 L, 243.1 L, 253.1 L, 340.2 L. Something stuck in joint at bottom of pipe 34.1 L .Possible sag 283-320 L. Deterioration/pitting throughout L. Crack near joint 108.8 L, fracture 195.6-196.5 L, crack near joint 233 L, fracture 311.4-313.6 bottom and side of pipe L, circumferential crack 337.3 L, multiple fractures 341.6 M. | 1974 | 50
139 | MEADE ST | L-6 | M-2 |  | M-1 | 327 | 315.4 | 8 | VCP | 3.08% | 2023 | 5% | 0 | 0 | 10 | 10 | 10 | 10 | 0 | 10 | 3 | 0 | 0 | 50 | RC2 | Point repair: PVC 2.7-7 w/offset joint L, 165.4 deposits settled compacted L, 86 root L. Root in joint 30.8 L, & 84.3 L. Joint offset 36.3 L, 41.5 L, 71.5 L, 161.9 M, 262 L, & 272.1 L. Deterioration at bottom of pipe throughout L. Sags/high spots throughout L. | 1964 | 60
164 | W 55TH AVE | L-5 | L-6B-1 |  | L-6B | 135.6 | 137.3 | 8 | VCP | - | 2023 | 5-15% | 0 | 0 | 0 | 10 | 10 | 10 | 10 | 10 | 3 | 0 | 0 | 50 | RC2 | Point Repair: PVC 0-4.7, joint missing pieces 4.1 L, roots in joint 5.4 L, sag 11-21 L, sag 39-46L, sag 71-87 M, 101-133 L, 127.3 Fracture Spiral L. Debris/encrustation throughout L. | -
168 | LOWELL BLVD | L-6 | L-6 |  | L-5A1 | 266 | 265.1 | 8 | VCP | 5.76% | 2023 | 10% | 20 | 0 | 10 | 0 | 0 | 0 | 20 | 0 | 3 | 0 | 0 | 50 | REG2 | Point Repair: PVC 0-8.3, possible infil bottom/side of pipe joint 72.3 L, 77.5 L, 87.2 L,107.6 L, 138.1 L, 147.5 L, 173.3 L, 245.1 L, 131.6 Crack Circumferential L, Point Repair: PVC 147.5-151.3 Joints Offset L, 200.7 Crack Circumferential L, 205.2 Crack Circumferential L, 224.9 Crack Longitudinal L, Point Repair: PVC 240.2-245.2 Joints Offset M, 257.8 Crack Multiple M | 1978 | 46
171 | LOWELL BLVD | L-6 | LH-1 |  | L-5A1 | 25 | 20.9 | 8 | PVC | 6.95% | 2023 | 5% | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | REG2 | UPSTREAM; Infiltration in MH LH-1 18.3 in invert connection: runner M | 2007 | 17
184 | W 53RD AVE | L-5 | STUB:I-3B |  | I-3 | 212.9 | 214.4 | 8 | VCP | - | 2023 | 5% | 0 | 0 | 0 | 10 | 10 | 10 | 10 | 10 | 3 | 0 | 0 | 50 | REG3 | 0.3 Crack Circumferential w/roots L, 9.2 roots L, 17.3 Deposits Attached Encrustation/joint deterioiration L , 82.9 roots L. Sag 113.9-123.8 L. Deposits/encrustation throughout L, pitting/deterioration throughout L. Not a proper cap at the end of the pipe/bricks. | -
186 | IRVING ST | L-5 | I-2 |  | I-1 | 330.5 | 330.2 | 8 | VCP | - | 2023 | 5% | 0 | 20 | 0 | 10 | 0 | 0 | 10 | 10 | 7 | 3 | 0 | 50 | RC3 | Point repair: PVC 0-12, 12.7 Crack Multiple L, 12.8 Roots Fine Joint L, 24.9 pitting in the bottom of pipe L, 25.6-30. Crack Longitudinal w/pitting/missing pieces M, 44.2 Crack Spiral L, 46.848 cracked/Broken Pipe Soil Visible M, pitting/piece missing 85.6, 122.7 138.5, 175, 183.9 L, crack in joint @ 172 L, 277.7 root L, 287.7 Roots Fine Joint L, 320.5 alignment: Right, 329.4 Crack Spiral L | -
215 | W 53RD AVE | L-5 | G6-1 |  | G-6 | 346.1 | 346.1 | 8 | VCP | - | 2021 | - | 0 | 0 | 10 | 10 | 0 | 10 | 10 | 10 | 11 | 5 | 0 | 50 | REG3 | Roots in joint @ 1 L, 39 L, 90 L, 96 L, 115 L, 208 L, 211 L, 220 L. Deterioration/pitting throughout L. Some cracks at the top of the pipe @ begining L, multiple fractures @ 39.1 L, longitudinal fracture @ 42.5 L & 45.4 L, roots in possible tap @ 77.2', circumferential fractures @ 96.2 L, 133.0 L, 169.4 L & 312.5 L, multiple fractures @208.9 L, fine roots on the top and side of tap @ 217.8 L, circuferentail fracture @ 218.5 L, longitudinal fracture @ 224.1 L, 227.4 L, 248.3 L & 282.4L , calcium deposit attached @ 312.5, point reair starting @ 332.0 - 334.9 offset L, material change to PVC @ 341.9 offset L. Outside drop @ 346.1. Possible candidate for lining. | -
219 | GROVE ST | L-5 | G-4 |  | G-3 | 412 | 414.4 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 10 | 10 | 20 | 0 | 10 | 7 | 0 | 0 | 50 | REG3 | Fine roots in tap @ 80.1 M, deposits attached @ 245.1 M & 285.2 M calcium. Sag @ 178-190 L, 370-385 L. Egging: Joint @ 141 L, 179 L, 192 L, 280 L, 398 L, | -
228 | W 55TH AVE | L-5 | G-3A |  | G-3 | 149 | 148.4 | 8 | VCP | 0.4% | 2019 | - | 0 | 0 | 10 | 0 | 10 | 0 | 10 | 20 | 1 | 0 | 0 | 50 | RC3 | Circumferential crack 3.3 L, sag 32-43 L, sag 97-107 L, deterioration 130-148 M, off set joint 148 L. Drop in MH G-3 | -
229 | GROVE ST | L-5 | G-3 |  | G-2 | 408 | 412.2 | 8 | PVC | - | 2021 | - | 20 | 0 | 0 | 0 | 10 | 20 | 0 | 0 | 7 | 0 | 0 | 50 | REG3 | Calcium deposits attached at joints @ 60.2 M w/infil: runner L & 65.8 L, 79.3 L. Egging: joint @ 75 (tap) L, 79 L, 105 L, 136 (tap) L, 160 L, 174 L, 187 L, 259 L, 334 (tap) L, 335 L, 348 L, 376 L, 392 L, end 414 L. Possible sag @ 46-66 L, 119-133 L, 145-160 L, 166-177 L, 200-221 L, 236-245, 252-262 L, 317-334 L, 334-349 L, 370-376 L, 390- 414 end L. Footage is wrong, several spots where the counter wasn't keeping up with the camera moving. | -
232 | W 55TH PL | L-5 | G-2A1 |  | G-2A | 162 | 162.6 | 8 | VCP | 0.4% | 2021 | - | 20 | 0 | 10 | 10 | 10 | 0 | 0 | 0 | 2 | 0 | 0 | 50 | REG3 | Point repair: PVC 134.8- 137. Possible sag @ approx. 9-18 L, 20-38 L, 76-84 L, 118-160 L. Roots in joint @ 33 L. Sealing ring failing/intruding M: 63.4 w/infil: dripper L, 68.6 L, 74.1 L, & 99.3 L. | -
248 | EASEMENT | L-5 | L-4C |  | L-4B | 298 | 297.4 | 8 | VCP | 0.4% | 2023 | 5-30% | 0 | 0 | 0 | 0 | 20 | 10 | 20 | 0 | 0 | 0 | 0 | 50 | H/RC3 | 2 CRACK M, 207.6-212 FRACTURE MULTI M. Deposits/encrustation throughout pipe L. Sags: 6-122 M, 200-208 M, 258-295 M. | 1977 | 47
270 | W 56TH AVE | M-4 | DM-1 |  | BE-53 | 363 | 367.1 | 10 | P.E. | 0.23% | 2021 | - | 0 | 0 | 0 | 0 | 40 | 10 | 0 | 0 | 4 | 0 | 0 | 50 | REG3 | Deposits/encrustation throughout. Water line is high (about 75%): seems like a sag from 20-114 M, also from 271-367 (MH). Camera under water from 293-300 & 340 until jetting comes back E. Note says: 4 BUCKETS OF DEBRIS REMOVED FROM LINE | -
352 | ROSEMARY LN | L-4 | BR-8B |  | BR-8A | 310 | 9.1 | 8 | VCP | - | 2021 | - | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | RC3 | Couldn't pass point repair & BR-8A has been paved over????/ Could not survey | -
354 | BRYANT ST | L-4 | BR-8 |  | BR-7 | 302 | 298.3 | 8 | PVC | 4% | 2021 | - | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 50 | REG3 | Up Stream; No Comments; BR-8-1 connection into MH has infil: runner M | -
384 | W 52ND AVE | L-3 | D-3B |  | D-3A | 399 | 395 | 8 | VCP | 4.8% | 2022 | - | 20 | 0 | 0 | 10 | 0 | 10 | 10 | 0 | 6 | 0 | 0 | 50 | RC1 | Some depoits through out L. Possible roots in joint @ 15.1 L, 19.9 L, 25.1 L, 30.1 L, 35.0 L, 40.0 L, 45.0 L, 74.6 M, 210.4 L. Possible Infil in joint @ 84.8 L, 100.0 L, & 114.7 L. Crack 134.9 @ 2 L & 348.3 @ 2 L. Possible candidate for lining | -
391 | ZUNI ST | L-3 | Z-24 |  | Z-23 | 302 | 300.4 | 8 | VCP | 0.6% | 2022 | - | 0 | 0 | 0 | 0 | 10 | 20 | 10 | 10 | 0 | 0 | 0 | 50 | REG1 | Camera starts out underwater for the first 6 ft; looks like a lot of grit in the bottom of the pipe. Crack/fracture at the bottom of the pipe @ joint 123 L, multiple/spiral fracture from 165-169 M, crack/fracture at the bottom of the pipe @ joint 287 L. Deterioration through out L. Possible sag/high spot from 0-27 L, 48-54 L, 57-61 L, 147-154 M, 157-165 M, 179-190 L, 194-200 L, 206-216 L, 228-236 L, 254-267 L, 276-287 M. Possible candidate for lining | -
394 | ZUNI ST | L-3 | Z-21 |  | Z-20 | 275.7 | 273.4 | 8 | VCP | 4.08% | 2022 | - | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 10 | 1 | 0 | 0 | 50 | REG1 | UPSTREAM; Infil stain around joint 12 @ 2 L, 38 @ 2 L, 42 circumference of pipe L, 94 @ 10 L, 114 circumference of pipe L, 105 @ 10 L, 170 circumference of pipe L, 195 circumference of pipe L, 211 both sides of pipe L, 246 @ 10 L. Encrustation @ 36.9 top of pipe L, 94.8 top of pipe M, 115.7 top of pipe L, 117.9 top of pipe L, 121.7 top of pipe L, 125.4 top of pipe L, at joint 160 possible infil M. Some deterioration throughout pipe L. Possible candidate for lining | 1973 | 51
415 | TEJON ST | L-3 | T-7 |  | T-6 | 311 | 309.3 | 8 | VCP | 2.24% | 2019 | - | 20 | 0 | 10 | 10 | 0 | 0 | 10 | 0 | 5 | 0 | 0 | 50 | RC1 | Roots in joint: 177.2 L, 187.1 L, 242.1 L. Offset joints: 302.4 L, 305.3 M. Multiple fractures 198.4-201.1 L. Possble infil bottom of joint 272.3 L. | 1978 | 46
416 | TEJON ST | L-3 | T-6 |  | T-5 | 52 | 49.5 | 8 | VCP | 3% | 2023 | 5% | 0 | 0 | 10 | 10 | 20 | 10 | 0 | 0 | 0 | 0 | 0 | 50 | REG1 | Sag 8-19 M, roots 42.7 L. Depoits/Encrustation throughout L. Joint offset 32.6. | -
457 | WYANDOT ST | M-3 | W-2 |  | W-1 | 291 | 290.4 | 8 | VCP | 1.4% | 2023 | 5-15% | 0 | 0 | 10 | 10 | 20 | 0 | 10 | 0 | 5 | 1 | 0 | 50 | H1 | Roots 13.6 L, 18.7 L, 23.7 L, 56.5 L, 71.8 L, 139.6 L, 155.2 L, 160.1 L, 165.1 L, 171 L, 176.1 L, 191.9 L. Sag 88-100 L, 281.8-289.5 M. Encrustation/possible infil in joint 86.3 L. Crack at top of pipe near joint 108.5 L & at tap 262.3 L. Point Repair: PVC 281.6-289.5 offset L. | 1970 | 54
20 | EASEMENT | L-7 | S-15 |  | S-14 | 260 | 259.3 | 12 | PVC | 0.2% | 2023 | 5% | 0 | 0 | 25 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 45 | REG2 | LOOKS LIKE FAT/GREASE HAS STUCK TO THE SIDES THROUGH OUT THE VIDEO. SAG 190-238 L. Egging joints thoughout L except: 88.2 M, 100 M, 111.6 M, 123.4 M, 147 M, 177.9 M, 220.9 M. | -
29 | EASEMENT | L-8 | S-12M |  | S-12L | 275 | 274.6 | 10 | PVC | 0.26% | 2023 | 10-40% | 0 | 0 | 25 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | REG2 | 21-30 SAG L, 33-65 SAG M, 36.8 EGGING M, 155-208 SAG L. Sag: 73-131 L, 225-266 L. Egging joints/out of round throughout pipe L-M | 1991 | 33
155 | KING ST | L-5 | K-5 |  | K-4 | 262 | 262.8 | 8 | VCP | 3.44% | 2023 | 0% | 0 | 0 | 0 | 25 | 0 | 20 | 0 | 0 | 7 | 0 | 0 | 45 | H/RC2 | 31.8-164.5 Deposits Attached Encrustation L-M, 169.6 Roots Fine Joint L, 189.9 Roots Fine Joint L, 204.3 Roots Fine Joint L, 219.9 Roots Fine Joint L, 224.8 Roots Medium Joint M, 240 Roots Fine Joint L, 244.9 Roots Medium Joint M, 250.7 Roots Fine Joint M, 255.1 Roots Fine Joint M. | -
194 | W 55TH AVE | L-5 | J-4B |  | J-4A | 400 | 436.6 | 8 | PVC | 0.4% | 2013 | - | 0 | 0 | 25 | 0 | 20 | 0 | 0 | 0 | 14 | 0 | 0 | 45 | REG3 | Sags thorughout L. Offset joint: 211.9 M, 215.1 M. ABANDONED DUE TO OFFSET 215.1. UPSTREAM; Sags: 101-161 M, 184-218 L. ABANDONED DUE TO OFFSET 218. | -
212 | W 53RD AVE | L-5 | G-6A |  | G-6 | 223 | 221.2 | 8 | VCP | - | 2021 | - | 0 | 0 | 25 | 10 | 0 | 0 | 10 | 0 | 3 | 0 | 0 | 45 | RC3 | Offset joint @ 81.6 M, point repair from 196.1 - 197.4, defective point repair @ 221.2 couldn't pass M. Material change @ 221.2 to PVC to the MH, outside drop.Roots in joint @ 5 L, 8 L. Crack at joint @ 11 L. NO UPSTREAM VIDEO/CAN SEE THE END. Survey abandoned @ 221.2. | -
247 | EASEMENT | L-5 | L-4D |  | L-4C | 307 | 307 | 8 | VCP | 0.4% | 2023 | 10-50% | 0 | 0 | 25 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | REG3 | UPSTREAM: 4 JOINT OFFSET M, SAG 20.5-30 M, SAG 263-END: 279.6’ CAM UNDER WATER M | 1977 | 47
357 | W 55TH AVE | L-4 | B-1C |  | B-1 | 153.9 | 153.9 | 8 | PVC | 0.4% | 2021 | - | 0 | 0 | 25 | 0 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 45 | REG3 | Material change @ 3.0: PVC offset M, material change @ 146.3: VCP. Deposits throughout L. Possible sag @ 120-150 M | 1976 | 48
360 | W 55TH AVE | L-4 | B-1 |  | A-3 | 327 | 332.2 | 8 | VCP | 0.4% | 2021 | - | 0 | 0 | 25 | 0 | 20 | 0 | 0 | 0 | 4 | 0 | 0 | 45 | REG3 | Localized repair: liner @ 49.6 - 53.1, material change: PVC 162.8 offset M, material change @ 170.6 VCP. Possible sag @ 18-52 M. | 1976 | 48
24 | W 53RD AVE | L-8 | S-12R |  | S-12Q | 285 | 283 | 8 | VCP | 0.36% | 2023 | 5-15% | 0 | 0 | 0 | 0 | 20 | 0 | 10 | 10 | 1 | 0 | 0 | 40 | REG2 | Sag 30-72 M, 228-256 M. Circumferential crack 180.4 L. Pitting/deterioration throughout L | -
57 | W 52ND PL | L-7 | TN-9A |  | TN-9 | 294 | 293.9 | 8 | VCP | 0.4% | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 0 | 10 | 10 | 6 | 5 | 0 | 40 | RC2 | BROKEN JOINT 72.7 L, 154 CRACK LONG L. Most of the joints are offset/out of alignment L. Sag: 40-53 L, 64-86 L, 111-146 L, 153-165 L, 171-186 L, 245-257 L. Deterioration/pitting throughout L. | -
80 | EASEMENT | L-6 | S-8 |  | S-7 | 400 | 398.5 | 15 | VCP | 0.22% | 2023 | 10% | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | REG2 | Sags: sags throughout L except 133-182 M, 243-273 E, 292-400 (end) E | 1973 | 51
81 | EASEMENT | L-6 | S-7 |  | S-6 | 140 | 359.8 | 15 | PVC | 0.22% | 2023 | 10% | 0 | 0 | 10 | 0 | 20 | 10 | 0 | 0 | 1 | 0 | 0 | 40 | REG2 | Sag: 13-97 M, 206-360 (end) M. Some joints throughout egging/deformed L, debris/encrustation throughout L | 1973 | 51
89 | RALEIGH ST | L-6 | R-3A1 |  | R-3A | 90 | 94.7 | 8 | VCP | - | 2023 | 5% | 0 | 0 | 0 | 10 | 0 | 10 | 10 | 10 | 3 | 0 | 0 | 40 | REG2 | UPSTREAM; Roots 21.7 L. Longitudinal crack 52.4 L, crack in bottom of pipe 56 L, pitting/deterioration bottom ofpipe 65.5 L. Deposits/encrustation in MH R-3A & from 46-73 L. | -
104 | EASEMENT | L-6 | Q-1 |  | Q-1A | 205 | 204.2 | 8 | DIP | 0.4% | 2023 | 5% | 20 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 40 | REG2 | Corrosion/deterioration throughout L. Possible sag 0-60 L, 138-182 L. Possible infil stains in joints: 44 L, 63.8 L, 83.9 L, 104 L, 122.4 L, 141.9 L, 158 L, 162.3 L, 182.3 L. | 1976 | 48
111 | PERRY ST | L-6 | P-3 |  | P-2 | 250 | 251.7 | 8 | VCP | 5.59% | 2023 | 5-10% | 0 | 0 | 10 | 0 | 10 | 0 | 20 | 0 | 5 | 0 | 0 | 40 | H/RC2 | 1 CRACK CIRC L, 128.5 FRACTURE CIRCUMFERENTIAL L, 145.6 CRACK CIRCUMFERENTIAL L, 147.8-152.9 MULTIPLE CRACK LONGITUDINAL HINGE M , POINT REPAIR: PVC 245-249 w/offset/sag L.GOOD PIPE TO BE LINED. | 1976 | 48
114 | OSCEOLA ST | L-6 | O-7 |  | O-6 | 350 | 349 | 8 | VCP | 4.28% | 2023 | - | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 10 | 12 | 0 | 0 | 40 | REG2 | Deposits/Encrustation 97-208 L, Deposits/encrustion in joint 74 L, 174.9 M, 270.5 L, 292 L, in joint: possible infil 282.7 M. Crack/pitting bottom 10 side 61 L, 79 L, in joint 153 L. Outside drop 343. | 1974 | 50
132 | W 54TH AVE | L-6 | N-1 |  | M-1A | 164 | 162.8 | 8 | VCP | 0.4% | 2023 | 5-20% | 0 | 0 | 0 | 10 | 20 | 0 | 10 | 0 | 5 | 0 | 0 | 40 | REG2 | Sags: 17-34 L, 38-55 L, 64-90 L, 116-152 M. Roots in joint 89.8 M. Circumferential crack 159 L | 1975 | 49
138 | MEADE ST | L-6 | M-3 |  | M-2 | 331 | 332.1 | 8 | VCP | 3.8% | 2023 | 5% | 20 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 4 | 0 | 0 | 40 | REG2 | Offset joints: 20.7 L, 56 L, 121.8 L, 126.9 L, 162.4 L, 187.4 L, 208.1 L, 212.8 L, 217.7 L. Deposits/encrustation throughout L, Point repair: PVC 74-78.1 w/offset & seperated joint L, 106.5 crack. Possible infil in joint 5.3 (large deposits), 131.3 in bottom of joint L, 172 in bottom of joint L, 197.5 (infil stain) L, 273.1 in bottom of joint L, 303.3 in bottom of joint L, 308.2 in bottom of joint L, 318.2 in bottom of joint L. | 1964 | 60
151 | KING ST | L-5 | K-9 |  | K-8 | 339.7 | 342.7 | 8 | VCP | - | 2023 | 0% | 20 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 6 | 0 | 0 | 40 | RC2 | Roots in MH K-9 M, roots in joints throughout L, 2 Crack Circumferential L, pitting/crack 17.7 L, 61.6 roots L , pitting/crack 77.3 L, 92.3 Crack Longitudinal w/infil stain L,infil stain around joint 121 L, possible infil stain top of pipe 288.5 L, 339 Crack Circumferential L | -
200 | W 55TH PL | L-5 | J-1A |  | J-1 | 213.8 | 213.8 | 8 | PVC | 0.465% | 2021 | - | 20 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 40 | REG3 | Possible infil inside MH J-1A next to invert L. Possible sags @ 31-38 L, 62-78 L, 84-95 L, 129-140 L, 181-212 end M. Possible egging thorughout: joints L. | -
233 | W 55TH PL | L-5 | G-2A |  | G-2 | 56 | 56.2 | 8 | VCP | - | 2021 | - | 0 | 0 | 10 | 0 | 10 | 20 | 0 | 0 | 0 | 0 | 0 | 40 | REG3 | Point repair: PVC @ 30.6-32.3. Possible sag @ 48-56 end L. A lot of grit in line M (before cleaning). Inside drop @ 56.2 offset L W/NO ACCESS FROM TOP | -
237 | EASEMENT | L-5 | L-4H |  | L-4I | 140 | 140.6 | 8 | VCP | 1.56% | 2023 | 5% | 0 | 0 | 0 | 0 | 20 | 10 | 10 | 0 | 0 | 0 | 0 | 40 | H1 | UPSTREAM; Point repair: PVC 0-6.3ft, 128.7ft Crack Circumferential L. Possible sag 0-15 M, 32-43 L, 69-80 M. Deposits/encrustation throughout pipe L. | -
243 | EASEMENT | L-5 | L-4G |  | L-4F | 351 | 346.7 | 8 | VCP | 4.54% | 2020 | - | 20 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 1 | 0 | 0 | 40 | H/RC3 | UPSTREAM; General Observation (bubbling seal?) 72.7 L. Infiltration in bottom of joints: 18.1 L, 23.8 L, 116.3 L, 121.5 L, 137.6 L, 148.2 L, 185.8 L, 223.1 L, 250.1 L, 266.3 L, 276.7 L, 282.2 L, 298.2 L, 303.6 L, 335.7 L. Deposits/encrustation throughout L. | 1977 | 47
341 | EASEMENT | L-4 | C-5C |  | C-5B | 177 | 174.8 | 8 | VCP | 5.4% | 2021 | - | 0 | 20 | 10 | 0 | 0 | 10 | 0 | 0 | 2 | 1 | 0 | 40 | REG3 | Break in bottom of joint @ 42.9 L. Deposits/encrustation thorughout L. Material change to PVC @165.2 to 173.8/ offset L; reduced size for approx 3' @ 173.8 going into MH | 1973 | 51
364 | W 54TH AVE | L-4 | A-3A |  | A-3 | 193 | 193.5 | 8 | VCP | 0.4% | 2021 | - | 0 | 0 | 0 | 10 | 10 | 10 | 10 | 0 | 3 | 0 | 0 | 40 | REG3 | Inside drop 193.4. Deposits throughout L; except near tap @ 90.4 M. Crack next to tap @ 1.6 w/roots L. Possible sag @ 9-34 L, 38-58 L, 61-87 L, & 147-169 L. Possible canidate for lining aside from sags. | 1976 | 48
378 | TEJON ST | L-3 | D-4A |  | D-4 | 194 | 192.4 | 8 | VCP | 2.1% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 10 | 3 | 0 | 0 | 40 | REG1 | Possible infil stain in joint @ 20, 35, 65, 105, 116, 126, 131, 136, 156, 170, 186; no infil observed. Deposits/encrustation through out L except 116-131 M. Deterioration through out L. Possible crack 68-70 @ 10 L. Possible candidate for lining | -
386 | W 52ND AVE | L-3 | D-3 |  | D-2 | 250 | 246.9 | 8 | VCP | 2.64% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 40 | REG1 | UPSTREAM: Deposits/grease attached throughout but heavy in some spots 5-26 & 55-110 Possible candidate for lining | -
417 | TEJON ST | L-3 | T-5 |  | T-4 | 330 | 332.9 | 8 | VCP | 3% | 2021 | - | 0 | 0 | 10 | 0 | 10 | 10 | 0 | 10 | 8 | 0 | 0 | 40 | RC1 | Deterioration/pitting: 0.0 hole L. Egged/deformed @ joint 15 L, 20 L, 46 L, 107 L, 113 L, 164 L. Off set joint @ 93 L, 103 L, 113 L, 118 L, 127 L, 158 L, 164 L, 184 L, 240 L, 292 L, 307 L. Sag @ 255-261 L. Calcium buildup on top of pipe @ joint 322 & 327 L. High water level at end of pipe going into MH. | -
429 | W 54TH PL | L-3 | V-9 |  | U-5 | 287 | 282.7 | 8 | VCP | 1.8% | 2022 | - | 0 | 0 | 10 | 0 | 10 | 20 | 0 | 0 | 3 | 0 | 0 | 40 | REG1 | Liner; point repair @ 0-4. Joint off set @ 65 L, 105 L, 111 L, 131 L, 151 L, 165 L, 171 L, 176 L, 226 L, 252 L. Possible sag @ 107-111 L, Deposits/encrustation through out L except @ 189-204 M & 225 M | 1963 | 61
437 | W 56TH AVE | L-3 | T-1 |  | U-1 | 333 | 330.9 | 8 | VCP | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 20 | 10 | 10 | 0 | 1 | 0 | 0 | 40 | REG1 | Possible vertical crack 23.6 @ 10 L, possible cracks 46.4 L, possible crack 62.6 L, possible crack 81.0 L, circumferential fracture 174.0 M, possible cracks 255.0 L. Sag @ 56.3-79.0 L, sag @ 81.9-89.9 L, sag @ 96.6-127.0 L, sag @ 134.0-173.0 L, sag @ 181.5-196.3 M, sag @ 201.4-238.1 M, sag @ 241.5-253.0 L, sag @ 256.4-274.1 L, sag @ 284.6-296.3 M, sag @ 299.7-323.0 L. Some deposits attached through out L. | 1976 | 48
451 | W MOFFAT PL | L-3 | V-4A |  | W-3C | 338 | 338 | 8 | P.E. | 3% | 2022 | - | 0 | 0 | 10 | 0 | 10 | 20 | 0 | 0 | 3 | 0 | 0 | 40 | REG1 | Deposits/grease attached throughout M. Egging/deformation @ 108-115 M & joint @ 138 L. Sag @ 232-250 L, 300-315 L. Material change: PVC @ 331. Drop @ 338 | -
458 | W 57TH PL | M-3 | W-1 |  | V-3 | 318 | 315.6 | 8 | PVC | 0.44% | 2022 | - | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 7 | 0 | 0 | 40 | REG1 | Whole pipe is egged/deformed M, deform/damage @ 74 L. Possible sag @ 41-53 L, 63-97 M, 152-170 L, 211-292 L | -
461 | W 58TH PL | M-3 | V-2A |  | V-2 | 272 | 270 | 8 | VCP | 0.4% | 2021 | - | 0 | 0 | 10 | 10 | 10 | 0 | 10 | 0 | 7 | 3 | 0 | 40 | RC1 | Material change: PVC 255; seperated joint L. Offset joints @ 22 L. Roots in joints @ 12 L, 22 L, 43 L, 47 L, 53 L, 75 L, 91 L, 96 L, 101 L, 106 L, 111 L, 116 L, 121 L, 126 L, 131 L, 136 L, 141 L, 147 L, 152 L, 157 L. Possible sag @ 0-38 L, 116-142 L. Fracture @ 18.7 top of pipe L, 128.7 @ 2 L, crack next to tap @ 170.2 L. POSSIBLE CANIDATE FOR LINING | 1970 | 54
465 | ZUNI ST | M-3 | Z-17 |  | Z-16 | 367 | 365.8 | 8 | VCP | 2.6% | 2023 | 5% | 20 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 4 | 1 | 0 | 40 | H/RC1 | UPSTREAM: Point repair: PVC 0-4.3. Point repair: liner 16-19.9. Roots in joint: 46.2 L, 62.3 L. Possible infil in joint: 72.7 L, 82.9 L, 93.2 L, 98.3 L, 111.6 L, 120.7 L, 125.8 L, 141 L, 166.2 L, 181.5 L, 212.1 L, 219.3 L, 317.3 L, 357.7 L. Circumferential crack 360.9 L. Deposit/encrustation throughout L. | 1970 | 54
483 | ALCOTT ST | M-4 | A-1B |  | A-1C | 446 | 445.4 | 8 | PVC | - | 2022 | - | 20 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 16 | 0 | 0 | 40 | REG1 | Possible sag @ 50.4-54.3 L, tap 194.2 @ 2 (break-in) possible infil on bottom L. Some deposits attached L. | -
529 | EASEMENT | N-3 | Z-1 |  | Z (meter station) | 160 | 154.1 | 15 | DIP | 0.3% | 2023 | 15-60% | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | REG1 | SAG: 41-88 E | 1970 | 54
92 | EASEMENT | L-6 | STR-1 |  | R-3A | 160 | 160 | 8 | PVC | - | 2023 | 5-15% | 0 | 0 | 25 | 0 | 10 | 0 | 0 | 0 | 1 | 0 | 0 | 35 | REG2 | Offset joint 143.1 M. Egging joints throughout L. Sag 135-143.1 L, 151.7-156L. Drop into MH R-3A | -
93 | RALEIGH ST | L-6 | R-3A |  | R-2 | 100 | 101 | 8 | VCP | 13.35% | 2023 | 5% | 0 | 0 | 0 | 25 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 35 | RC2 | DEPOSITS/ENCRUSTATION THROUGHOUT PIPE, 63.5 ROOTS IN JOINT L, 67.4 ROOTS IN JOINT M, 87.3 ROOTS IN JOINT L, OUTSIDE DROP 98.9. MH R-3A has Deposits/ensrutation in the invert/narrowing L. | -
179 | JULIAN ST | L-5 | J-9 |  | J-8 | 176 | 174.8 | 8 | VCP | 3.8% | 2021 | - | 0 | 0 | 25 | 0 | 0 | 10 | 0 | 0 | 4 | 3 | 0 | 35 | REG3 | Deposits/encrustation attached thorughout L, offset/broken joint @ 157.2 M | -
226 | W 55TH AVE | L-5 | G-3B |  | G-3 | 328 | 330.4 | 8 | VCP | 0.4% | 2021 | - | 0 | 0 | 25 | 0 | 10 | 0 | 0 | 0 | 3 | 0 | 0 | 35 | REG3 | Light sagging throughout @ 41-67 L, 91-127 L, 155-211 L, 222-233 L, 245-256 L, 260-270 L, 288-301 L, 331-327 L. Material change: PVC @ 327 offset M. Outside Drop before MH @ 330.3. May be a good candidate for lining. | 1977 | 47
242 | EASEMENT | L-5 | L-4I |  | L-4G | 161 | 162.6 | 8 | VCP | 1.56% | 2021 | - | 0 | 0 | 25 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 35 | REG3 | PVC to approx. 5.3/material change to VCP, possible joint sepperation? M, circumferential fracture (multiple) @ approx. 160 L. Good canidate for lining | -
366 | ALCOTT ST | L-4 | A-2 |  | A-1 | 402 | 401.9 | 8 | VCP | 3.36% | 2021 | - | 0 | 0 | 25 | 10 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 35 | RC3 | Roots in joint @ approx. 29, 44, 49, 75, 85, 146, 171, 176, 181, 196, 201, 206, 211, 221, 236, 273, 294, 299, 309, 314, 319, 324, 344, 354, 370, 380 all L. Point repair: PVC @ apprx. 389-392 off set on 389 joint M. Possible canidate for lining aside from the off set and sag at the end. | 1976 | 48
413 | W 53RD AVE | L-3 | T-8A |  | T-8 | 320 | 318.4 | 8 | VCP | 1.6% | 2022 | - | 0 | 0 | 25 | 10 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 35 | REG1 | Upstream: Joint offset: 39 L, 44 L, 55 L, 60 L, 65 M, 70 M, 75 M, 80 M, 85 L, 90 L, 95 M, 100 L, 110 M, 115 M, 120 M, 125 M, 140 L, 170 L, 175 M, 215 L. Roots in joint @ 134 L. Possible candidate for lining | 1978 | 46
419 | WYANDOT ST | L-3 | W-6 |  | W-5 | 68 | 65.7 | 8 | VCP | 0.4% | 2023 | 5% | 0 | 0 | 0 | 25 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | REG1 | Roots 30.9 L, 35.1 L, 40.3 L, 61.5 L. Sag 33.4-61.5 L. Roots in MH W-5 M. | -
18 | EASEMENT | L-7 | S-17 |  | S-16 | 152 | 149.2 | 12 | P.E. | 0.22% | 2023 | 10% | 20 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | REG2 | 9.5 INFILL WEAPER L, 22.3 INFILL WEAPER L, Point repair: PVC 53.4-78.2 w/offset joint L. g | -
19 | EASEMENT | L-7 | S-16 |  | S-15 | 336 | 337.7 | 12 | PVC | 0.2% | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 30 | REG2 | Some sagging throughout L, some joints throughout egging/deformed L, debris/encrustation throughout L | -
32 | EASEMENT | L-8 | S-12J |  | S-12I | 350 | 347.1 | 12 | PVC | 0.48% | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 30 | REG2 | Debris/encrustation througout L, joints throughout egging/deformed L, sags throughout L | -
42 | EASEMENT | L-7 | S-12C |  | S-12B | 297 | 295.3 | 12 | VCP | 0.45% | 2023 | 10-15% | 0 | 0 | 0 | 0 | 20 | 0 | 10 | 0 | 0 | 0 | 0 | 30 | REG2 | 127.4-140 SAG M, FRACTURE CIRC. 187.1. Sag: 0-45 L, 184-201 L, 268-289 L. Crack at top of pipe 0 L, 22.4 L, 28.7 L, 206.1 L, 247.6 L. Circumferential crack 120.3 L, 126.1 L, 185.6 L, 274.4 L. Camera was having some problems getting through: grit? | -
121 | EASEMENT | L-6 | O-3 |  | O-2 | 63 | 67.5 | 8 | DIP | 44.72% | 2023 | 5% | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0 | 0 | 30 | RC2 | Corrosion throughout pipe L. Possible infil in joint 26.1 L, 43.9 L | 1974 | 50
122 | EASEMENT | L-6 | O-2 |  | O-1 | 125 | 114.7 | 8 | VCP | 5.27% | 2023 | 5% | 0 | 0 | 0 | 10 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 30 | RC2 | UPSTREAM; Roots in joints: 24.6 L, 29.5 L, 39.6 L, 59.8 L, 65.1 L, 105.4 L, 100.3 L, 110.4 L. Multiple longitudinal hinge cracks 105.4-110.4 M. LINNING WOULD DO GREAT. | 1974 | 50
127 | LOWELL BLVD | L-6 | S-1 |  | L-2 | 311 | 310.3 | 15 | VCP | 0.22% | 2023 | 10% | 20 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 30 | REG2 | Possible infil stain at joint 63 M (none observed), Point repair: PVC 303.3. Deposits/ecrustation attached throughout pipe at the water line: grease? L | 1973 | 51
143 | LOWELL BLVD | L-6 | L-12 |  | L-11 | 331 | 56.2 | 8 | VCP | 5.77% | 2023 | 5% | 20 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 2 | 0 | 0 | 30 | REG2 | Circumfernetial crack w/infil 4 L, possible infil bottom of pipe in joint @ 8.5 L, 18.7 L, 23.8 L, 29.1 multiple fractures L, circumferential crack w/infil 30.1 L, tap 47.3 @ 10 potential infil at bottom seal L, 52.2 crack circumferential w/infil L | -
144 | LOWELL BLVD | L-6 | L-11 |  | L-10 | 56 | 321.9 | 8 | VCP | 4.7% | 2023 | 5% | 20 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 11 | 1 | 0 | 30 | REG2 | 150.7 Infiltration Weeper Joint L, 188.9 Infiltration Weeper capped tap L, Point Repair: PVC 225.2-230.5 offset L. | -
145 | W 53RD AVE | L-5 | K-3A |  | K-3 | 322 | 327.6 | 8 | PVC | - | 2023 | 5-10% | 0 | 0 | 10 | 0 | 10 | 10 | 0 | 0 | 4 | 0 | 0 | 30 | REG2 | Difficulty getting into line because of compacted deposits? Egging/deformation throught out L. 228.3ft Intruding Sealing Material Sealing Ring Loose/Poorly Fitting M, 228.8ft Survey Abandoned due to intruding gasket. UPSTREAM VIDEO; Sag 0-24 L, 106-121 L. | -
160 | W 55TH AVE | L-5 | L-6C-1 |  | L-6C | 293 | 292.8 | 8 | VCP | 0.4% | 2023 | 5-15% | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 10 | 6 | 0 | 0 | 30 | REG2 | Point Repair: PVC 0-3.9, high spot 0-5.5 L, sag 8.6-25.8 L, buldge in side of pipe 9 oclock side L, sag 82-97 L, sag 123-132 L, 105.8 root L, 111 root L, roots in joint 116.4 L, 174-188 Sag L, roots in joint 181.8 L, sagging 217-264 L. | -
172 | LOWELL BLVD | L-6 | L-5A1 |  | L-5 | 132 | 130.9 | 8 | VCP | 5.76% | 2023 | 10-15% | 0 | 0 | 0 | 0 | 20 | 0 | 10 | 0 | 0 | 0 | 0 | 30 | REG2 | 1.2 ft. Circumferential fracture L. Sags 0-21 M, 38-91 L, 107-206 L, 209-232 M. | 1978 | 46
182 | JULIAN ST | L-5 | J-7 |  | J-6 | 325 | 81.4 | 8 | VCP | 3.8% | 2017 | - | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 10 | 1 | 2 | 0 | 30 | RC3 | UPSTREAM; Break or hole in bottom of pipe joint 2.1 L. Deterioration/pitting & debris throughout L. ABANDONED: INTRUDING TAP 81.4, DIDN'T GO DOWNSTREAM. | -
191 | JULIAN ST | L-5 | J-5 |  | J-4 | 26 | 26.1 | 8 | DIP | 2.28% | 2013 | - | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 0 | 0 | 0 | 30 | REG3 | Deterioration throughout M. Possible circumferential crack 14.1 L. | 1976 | 48
201 | W 55TH PL | L-5 | J-1 |  | L-5B | 415 | 415.6 | 8 | PVC | 0.89% | 2021 | - | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 10 | 5 | 0 | 0 | 30 | REG3 | Offset joint @ approx. 2.5 L, possible sag at approx. 67-72 L, 138-150 L, & 185-195 L. Joints @ approx. 181 L, 254 L, 266 L, 289 L, 326 L, & 399 L looks like they might be egged, end MH connection was clay & looks like it might be offset/broken. | 1978 | 46
203 | W 55TH PL | L-5 | L-5A |  | L-5 | 245 | 248.3 | 8 | VCP | 0.4% | 2023 | 5-15% | 20 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 30 | REG3 | 1.2 Circumferential crack L. Circumferential crack 32.2 L, 126.2 spiral crack L. Possible infil in bottom of joint 55, 65, 70, 75, 95, 105 L. | 1978 | 46
213 | GROVE ST | L-5 | G-8 |  | G-7 | 235 | 235.5 | 8 | PVC | - | 2021 | - | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 10 | 5 | 0 | 0 | 30 | REG3 | Calcium build up at the start of pipe L, point repair (metal?) @ 138.4 -140.2, pipe out of round & possible break @182.9 L | -
217 | GROVE ST | L-5 | G-5 |  | G-4 | 327 | 328.9 | 8 | PVC | - | 2021 | - | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 10 | 5 | 0 | 0 | 30 | REG3 | Intruding sealing ring on bottom of pipe @ 3.0 L, sag @ 198-224 L, 273-289 L, 297-302 L. Egging: joint @ 54 L, 57 L, 66 L, 79 L, 145 L, 172 L, 275 L. | -
218 | W 54TH AVE | L-5 | STUB:G-4 |  | G-4 | 249 | 252.6 | 8 | VCP | - | 2014 | - | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 10 | 3 | 1 | 0 | 30 | RC3 | UPSTREAM; Drop into MH G-4. Deterioraton/pitting throughout L. Hole in top of pipe where rock was pushed in 198.3 L. Cap at end is just brick. | -
222 | W 54TH AVE | L-5 | G-3F |  | G-3E | 28 | 24.4 | 8 | PVC | 0.4% | 2021 | - | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 10 | 0 | 0 | 0 | 30 | REG3 | Sag from 15-24 w/possible egging L. Grit in line L. Looks ok | 1983 | 41
223 | EASEMENT | L-5 | G-3E |  | G-3D | 111 | 110.3 | 8 | VCP | 3.24% | 2021 | - | 0 | 0 | 10 | 0 | 10 | 10 | 0 | 0 | 1 | 0 | 0 | 30 | REG3 | Sag from 104-108 L: offset joint L. Deposits/encrustation: Calcium throughout L. | 1977 | 47
239 | EASEMENT | L-5 | L-4L |  | L-4K | 184 | 184.8 | 8 | PVC | - | 2019 | - | 0 | 0 | 0 | 0 | 20 | 10 | 0 | 0 | 0 | 0 | 0 | 30 | REG3 | Encrustation/deposits attached: grease throughout pipe L. Deposits/encrustation at joint 39.5 & 52.0 possible infiltration L. Sags: 26-45 M, 77-82 L, 113-125 L, 133-148 L, 164-181 M. | -
249 | EASEMENT | L-5 | L-4B |  | L-4A | 268 | 268.2 | 8 | VCP | 0.4% | 2023 | 10-30% | 0 | 0 | 0 | 0 | 20 | 0 | 10 | 0 | 0 | 0 | 0 | 30 | H1 | Sags: 20-47 M, 52-64 M, 80-123 M, 130-213 M, 218-268 END M. Circurferential crack: 38.3 L, 51.4 L, 60.8 L, 66.2 L, 71.9 L, 87.9 L, 93.5 L, 109.6 L, 120.3 L, 147 L, 168.2 L, 173.3 L, 216.8 L ALL LOOK LIKE THEY'RE FROM ROOT CUT SAW. | 1977 | 47
262 | EASEMENT | L-4 | DM-7 |  | DM-6 | 330 | 329.1 | 8 | PVC | - | 2023 | 5% | 20 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 30 | H/RC3 | Some egging/out of round joints throughout L, 328.9ft DM-7 buried, Infiltration runner in DM-7 L at the invert connection | -
263 | W 55TH AVE | L-4 | DM-6 |  | DM-5 | 250 | 251.6 | 8 | PVC | 0.49% | 2021 | - | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 10 | 5 | 0 | 0 | 30 | REG3 | Joints look egged @ 35 L, 72 L, 85 L. Egged pipe @ approx. 145-158, 201 L (tap). Sag @ 21-41 L, 66-85 M, 138-152 M. | 1983 | 41
271 | W 56TH AVE | M-4 | BE-53 |  | BE-52A | 288 | 288.7 | 10 | P.E. | 0.23% | 2021 | - | 0 | 0 | 0 | 0 | 20 | 10 | 0 | 0 | 3 | 0 | 0 | 30 | REG3 | Pipe about 25% full until 38', sag from approx. 50-59 L, 100-165 M, 180-215 L, 224-to end 288 E. Deposits/encrustation throughout L. Note says: 3 BUCKETS OF DEBRIS REMOVED FROM LINE | -
359 | BEACH CT | L-4 | B-2 |  | B-1 | 312.4 | 356.1 | 8 | VCP | 3.88% | 2023 | 5-10% | 0 | 0 | 0 | 10 | 0 | 10 | 10 | 0 | 7 | 1 | 0 | 30 | H/RC3 | Roots throughout in joints L except: 11.1 Roots Medium Joint. Debris/encrustation throughout L. 262.8 Crack Circumferential L. 349-354 Point Repair: Liner. 354.3ft inside drop connection | -
397 | W 56TH AVE | M-4 | BE-49B |  | Z-18 | 51 | 50 | 8 | VCP | - | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 0 | 10 | 0 | 2 | 0 | 0 | 30 | REG1 | Point repair: PVC 0-4, offset/seperated joint @ 4 L. Sag 37-47 L. 47.1 ft. Crack Circumferential L | -
405 | EASEMENT | L-3 | T-8E-1 |  | T-8E | 50 | 40 | 8 | VCP | 2.8% | 2022 | - | 0 | 0 | 10 | 10 | 0 | 0 | 10 | 0 | 1 | 0 | 0 | 30 | RC1 | UPSTREAM: Possible crack at top of pipe @ 35 L. Off set joint @ 1 M. Roots in joint @ 1 L. | 2019 | 5
421 | W 54TH AVE | L-3 | W-4A |  | W-4 | 132 | 191.2 | 8 | VCP | 4.32% | 2023 | 5% | 20 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 4 | 0 | 0 | 30 | REG1 | UPSTREAM: Point Repair: PVC 80.9-85.6. Deposit/encrustation around joint; possible infil 3 L, 40.2 L. Possible infil in bottom of joint 5 L, 24.9 L, 35.3 L. | 1972 | 52
430 | W 54TH AVE | L-3 | U-7A |  | U-7 | 130 | 115.7 | 8 | VCP | 3.75% | 2023 | - | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 0 | 2 | 0 | 0 | 30 | REG1 | Point Repair: Liner 33.2-37.3. Point repair: PVC 74.8-76.8. Roots in joint: 24.2 L, 30 L, 44.2 L, 49.1 L, 54.3 L, 104.6 L, 109.6 L. Deposits/encrustation 74.8-76.8 L. Sag 79-90 L. | -
436 | TEJON ST | L-3 | T-2 |  | T-1 | 218 | 216.5 | 8 | VCP | 2% | 2022 | - | 0 | 0 | 10 | 0 | 10 | 0 | 10 | 0 | 1 | 0 | 0 | 30 | REG1 | Possible sag 9.3-15.4 L, possible sag @ 24.9-30.6 L. Crack 24.0 @ 12 next to joint L, possible crack 44.1 @ 12 next to joint L. Joint offset slightly 69.8 L, 74.6 L, 79.5 L, 94.5 L, 119.6 L, 169.3 L, 174.6 L, 204.3 L. Brick in the invert of downstream, looks like to divert from old invert. | 1978 | 46
443 | VALLEJO ST | L-3 | V-8 |  | V-7 | 174 | 173.7 | 8 | VCP | 5.1% | 2022 | - | 0 | 0 | 10 | 0 | 0 | 10 | 10 | 0 | 5 | 0 | 0 | 30 | REG1 | Liner; point repair @ 12.9-16.7. Crack next to tap 17.4 @ 10 L. Depostis/encrustation throughout; joint @ 71, 86, 118 has some calcium build up L. Material change @ 165 PVC; Joint offset M. | -
464 | ZUNI ST | L-3 | Z-18 |  | Z-17 | 140 | 142 | 8 | VCP | 1.6% | 2023 | 5% | 0 | 0 | 0 | 10 | 10 | 10 | 0 | 0 | 1 | 0 | 0 | 30 | RC1 | UPSTREAM: Roots joint 1.9 L. Sag 3-17 L, 23-34 L, 50-60 L, 81-90 L, 105-116 L. Deposits/encrustation throughout L. | 1973 | 51
517 | W 60TH AVE | M-4 | Z-5H |  | Z-5G | 280 | 280 | 8 | PVC | - | 2022 | - | 0 | 0 | 10 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 30 | REG1 | Egging/deformed joint @ 179 L, 193 L, 207 L, 235 L, 249 L. Sag @ 29-50 L, 73-82 L, 115-124 L, 197-226 L, 232-255 L, 268-276 L. Grit in the line L | 2016 | 8
519 | W 60TH AVE | M-4 | Z-5F |  | Z-5E | 191 | 190.5 | 8 | PVC | - | 2022 | - | 0 | 0 | 10 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 30 | REG1 | Sag @ 3-31 L. Egging/deformed joint @ 63 L. Some grit & rock in the line L | 2016 | 8
526 | EASEMENT | N-3 | Z-4 |  | Z-3 | 304 | 303.3 | 18 | PVC | 0.3% | 2018 | - | 20 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | REG1 | Point repair: liner 53.1; looks like an infil stain next to joint L. Egging/out of round through out pipe L. | 1970 | 54
107 | PERRY ST | L-6 | P-6A |  | P-6 | 150 | 146.2 | 8 | PVC | 4.92% | 2023 | 5% | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 25 | REG2 | Egging/deformed pipe: 36 L, 61.8 L, 71.4 L, 85.5 M, 109.8 M, 123.6 L. | 1991 | 33
154 | LOWELL BLVD | L-5 | L-9 |  | CC 45A.10 (METRO) | 30 | 30 | 8 | VCP | - | 2023 | 5% | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | REG2 | Point repair: PVC 22.8-27.2 w/offset joint M. Outside drop 27.2 | -
329 | COLUMBINE RD | L-4 | C-8A |  | C-8 | 30 | 28.6 | 8 | VCP | - | 2021 | - | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | REG3 | Point repair starting @ 26.7 to drop/ offset M. Outside drop @ 27.7 | -
471 | W 58TH AVE | M-3 | Z-14A |  | Z-14 | 264 | 268.1 | 8 | VCP | 0.6% | 2022 | - | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 7 | 4 | 0 | 25 | REG1 | UPSTREAM: Roots in joint @ 36 M, 41 M, 46 M, 51 M, 56 M, 61 M, 67 M, 71 M, 77 M, 81 L, 87 M, 92 L, 97 M, 99 M, 101 L, 106 L, 116 L, 121 L, 126 M, 142 M, 147 L, 152 L, 159 L, 179 L, 184 L, 194 L | 1970 | 54
2 | EASEMENT | M-8 | S-28B |  | S-28A | 185 | 183.8 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 3 | 0 | 0 | 20 | REG2 | Some sagging throughout L, some joints throughout egging/deformed L | -
10 | EASEMENT | M-8 | S-23 |  | S-22 | 37 | 38.4 | 8 | VCP | 2% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 20 | REG2 | UPSTREAM// Circumferential crack 5 L. Deposits/encrustation on bottom of pipe 31 L. | 1982 | 42
22 | EASEMENT | L-7 | S-13 |  | S-12 | 390 | 392 | 12 | DIP | 0.2% | 2023 | 5% | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 20 | REG2 | Sag: 201-391 (end) L, surface damage/corrosion throughout L | -
23 | W 53RD AVE | L-8 | S-12S |  | S-12R | 152 | 151.2 | 8 | VCP | 0.4% | 2023 | 5-10% | 0 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 2 | 0 | 0 | 20 | REG2 | UPSTREAM: Sag 126-132 L. Circuferential crack 111.8 L. | -
31 | EASEMENT | L-8 | S-12K |  | S-12J | 357 | 346.6 | 12 | PVC | 0.48% | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG2 | Joints throughout egging/deformed L, sags throughout L | -
33 | EASEMENT | L-8 | S-12I |  | S-12H | 158 | 158.1 | 12 | PVC | 0.48% | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 1 | 0 | 0 | 20 | REG2 | MH 158’ W/INFILL AT LATTER END (MH lined in 2023). Joints egging/out of round throughout pipe L. Sag 62-133 L. | -
34 | EASEMENT | L-8 | S-12H |  | S-12G | 150 | 149.8 | 12 | PVC | 0.48% | 2023 | 5-10% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG2 | Sags: 23-43 L, 133-149 (end)M. Joints throughout egging/deformed L | -
39 | EASEMENT | L-7 | S-12F |  | S-12E | 155 | 155.6 | 12 | PVC | 0.62% | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 20 | REG2 | UPSTREAM: DIP 94 TO END W/CROSION M | -
40 | EASEMENT | L-7 | S-12E |  | S-12D | 314 | 316 | 12 | PVC | 0.45% | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG2 | Some sagging throughout L, some joints throughout egging/deformed L | -
41 | EASEMENT | L-7 | S-12D |  | S-12C | 383 | 385 | 12 | PVC | 0.45% | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG2 | Some sagging throughout L, some joints throughout egging/deformed L | -
43 | EASEMENT | L-7 | S-12B |  | S-12A | 123 | 121.9 | 12 | VCP | 0.39% | 2023 | 10% | 0 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 20 | REG2 | ALL JOINTS ARE CRACKED CIRC L, GOOD PIPE TO HAVE LINED. Sag: 43-56 L, 72-121 L. Crack near joint 13.8 L, 53.4 L, 87.2 L | -
46 | EASEMENT | L-7 | S-11 |  | S-10 | 399 | 398.1 | 12 | PVC | 0.22% | 2023 | 10% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG2 | FROM 0-128 SAG L, SAG 160-179. Egging/out of round joints throughout L | 1973 | 51
49 | TENNYSON ST | L-7 | TN-1 |  | TN-2 | 90 | 86 | 15 | VCP | 0.4% | 2023 | 10% | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG2 | UPSTREAM: 82 INFILL WEEPER L | 1973 | 51
53 | STUART ST | L-6 | ST-2 |  | ST-1 | 138 | 141.3 | 8 | VCP | 4.32% | 2023 | 5% | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 3 | 0 | 0 | 20 | REG2 | Roots 11 L, 16 L, 21.6 L.2.2. Circumferential fracture L. | -
54 | W 53RD AVE | L-6 | ST-1 |  | TN-6 | 335 | 333.6 | 8 | PVC | 4.5% | 2023 | 5% | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 4 | 0 | 0 | 20 | REG2 | MATERIAL CHANGE TO DIP 224.5-242.3 Corrosion L. Egging joints: 78.8 L, 194.9 L, 290.4 L, | -
58 | TENNYSON ST | L-6 | TN-9 |  | TN-8 | 260 | 246.3 | 8 | VCP | - | 2023 | 5% | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | 4 | 3 | 0 | 20 | RC2 | POINT REPAIR: PVC 121.9-125.5, 243.2 ROOTS L. Deterioration/pitting through out L. | -
71 | EASEMENT | L-7 | TN-8B |  | TN-8A | 87 | 85.9 | 8 | CIP | 0.4% | 2023 | 5-10% | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG2 | Sag 28-85 M. Lined in 2023 after video. | -
88 | RALEIGH ST | L-6 | R-3 |  | R-3A1 | 15 | 16 | 8 | DIP | - | 2023 | 5% | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 20 | REG2 | Point repair 0-3.6 w/offset L, Corrosion from 3.6 through remainder of pipe | -
117 | OSCEOLA ST | L-6 | O-4 |  | O-3A | 22 | 23.4 | 8 | VCP | 3.48% | 2023 | 5-10% | 0 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 1 | 0 | 0 | 20 | H/RC2 | UPSTREAM: Sag 0-19 M. Circumferential crack 19.7 L. | -
120 | OSCEOLA ST | L-6 | O-3A |  | O-3 | 190 | 189.1 | 8 | CIP | 3.48% | 2023 | 5-10% | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 2 | 1 | 0 | 20 | RC2 | Lined in 2023 after video. | -
129 | NEWTON ST | L-6 | N-4 |  | N-3 | 320 | 317 | 8 | CIP | 5.6% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | 9 | 0 | 0 | 20 | REG2 | .8ft delaminating of lining L, deposits/encrustation throughout pipe L | -
131 | NEWTON ST | L-6 | N-2 |  | N-1 | 300 | 303.7 | 8 | VCP | 2.2% | 2023 | 5% | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 5 | 0 | 0 | 20 | RC2 | UPSTREAM; 22ft root L. Circumferential crack 298.6 L. | -
135 | MEADE ST | L-6 | M-6 |  | M-5 | 126 | 123.7 | 8 | CIP | 3.68% | 2023 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | 3 | 0 | 0 | 20 | REG2 | 0 lining delaminating, 109-112.9 lining delaminating L. Deposits/encrustation throughout L. | 1964 | 60
142 | LOWELL BLVD | L-6 | L-13 |  | L-12 | 257 | 255.5 | 8 | VCP | - | 2023 | 5-10% | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 4 | 2 | 0 | 20 | REG2 | 14.2-24.7 Deposits settled compacted M, deposits/encrustation throughout pipe L. | -
153 | W 54TH AVE | L-5 | K-7 |  | L-9 | 264 | 265.5 | 8 | VCP | 0.4% | 2023 | 5-15% | 0 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 3 | 0 | 0 | 20 | REG2 | 2.7 Crack Circumferential L, multiple sags throughout L | 1971 | 53
159 | W 55TH AVE | L-5 | L-6D |  | L-6C-1 | 26 | 95.1 | 8 | VCP | 2.28% | 2023 | 5-15% | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 2 | 0 | 0 | 20 | REG2 | UPSTREAM; Point repair: PVC 0-3,sag/belly 0-28 M, sag 32-80 L | -
161 | W 55TH AVE | L-5 | L-6C |  | L-6B-1 | 98 | 97.3 | 8 | VCP | 0.4% | 2023 | 5% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG2 | Sag 7-14 L, 22ft-32 Sag L, sag 49-62 L, sag 75-88 L, Point Repair: PVC 93.5-97.3 w/offset joints L | -
165 | W 55TH AVE | L-5 | L-6B |  | L-6A | 103 | 102.4 | 8 | VCP | 0.4% | 2023 | 5% | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 2 | 0 | 0 | 20 | REG2 | Roots in joint 0.1 L, 13.1ft root L, 93.8 ft. Crack Circumferential L | -
166 | LOWELL BLVD | L-5 | L-6A |  | CC 45A.8 (METRO) | 50 | 32.3 | 8 | VCP | 0.8% | 2023 | 15% | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG2 | UPSTREAM; Point Repair: PVC 0-5.5ft, possible infil in bottom/side of pipe 9.5 L, | 1978 | 46
187 | W 54TH AVE | L-5 | I-1A |  | I-1 | 351.6 | 351.2 | 8 | PVC | 0.4% | 2023 | 5-10% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 3 | 1 | 0 | 20 | REG3 | UPSTREAM; Joints throughout possibly egged L. Sags throughout L. | -
211 | W 53RD AVE | L-5 | G-6B |  | G-6A | 164 | 164.6 | 8 | VCP | - | 2021 | - | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 3 | 3 | 0 | 20 | RC3 | Roots in joint @ 18 L, 75 L, 82 L, 91 L, 103 L, 115 L, 127 L, 133 L, 142 L, 151 L. Roots in tap @71.6 M. Multiple fracture @ 82.0 L, circumferential crack @ 130.0 L, crack @ 153.9 L. Possible candidate for lining | -
214 | GROVE ST | L-5 | G-7 |  | G-6 | 175 | 192.2 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 20 | REG3 | Possible egging: joint @ 45 L, 58 L, 85 L, 97 L, 111 L, 125 L, 143 L, 164 L, 190 L. Sag @ 190-192 end L. Outside drop @ 192.2 | -
216 | GROVE ST | L-5 | G-6 |  | G-5 | 325.6 | 325.6 | 8 | PVC | - | 2021 | - | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 6 | 0 | 0 | 20 | REG3 | Furnco at start of pipe, offset joint @ approx. 1.0 L. Egging: joint @ 60 L, 193 L, 206 L, 245 L, 272 L, 284 L, 309 L. | -
225 | EASEMENT | L-5 | G-3C |  | G-3B | 285 | 287.7 | 8 | VCP | 2.16% | 2021 | - | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 4 | 0 | 0 | 20 | REG3 | UPSTREAM// Possible sag @ 34-44 L, 86-99 L, 107-121 L. Deposits/encrustation: calcium throughout L. | 1977 | 47
235 | W 55TH PL | L-5 | G-1 |  | L-4H | 347 | 346.1 | 8 | VCP | 3.52% | 2021 | - | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 2 | 0 | 0 | 20 | RC3 | Circumferential fracture @ 343.1 w/roots L. Roots in joint @ 194 L, 205 L, 210 L, 215 L, 232 L, 237 L, 248 L, 264 L, 269 L, 296 L, 302 L. Possible candidate for lining. | 1977 | 47
241 | EASEMENT | L-5 | L-4J |  | L-4I | 331 | 328.6 | 8 | PVC | - | 2020 | - | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 1 | 0 | 0 | 20 | H1 | UPSTREAM; Sag: 124-139 L, 175-187 L. Deposits/encrustation throughout (grease) L. | -
246 | EASEMENT | L-5 | L-4E |  | L-4D | 169 | 212.6 | 8 | VCP | 0.4% | 2023 | 10% | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | RC3 | UPSTREAM: ¼ FULL THROUGH OUT – 69’ CAM UNDER WATER BECAUSE OF SAG | 1977 | 47
269 | EASEMENT | L-4 | DM-2 |  | DM-1 | 194 | 196.8 | 8 | PVC | 0.46% | 2021 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 1 | 0 | 0 | 20 | RC3 | UPSTREAM// Sags @ 0-25 L, 53-75 L, 93-106 L, & throughout 113-195 end M. Egging throughout: joints @ 87 L, 100 L, 113 L, 126 L, 133 L (tap), 139 L, 151 L, 164 L, 176 L, 189 L. Note says: UPSTREAM MH DM-2 IS UNDER A FENCE, NO ACCESS, NO DEPTH | 1983 | 41
275 | W 56TH AVE | M-4 | BE-52 |  | BE-51 | 408 | 412 | 10 | P.E. | 0.23% | 2021 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 7 | 0 | 0 | 20 | REG3 | Possible sags @ 49-60, 94-105, 166-204, 233-255, 377-405: all L. Possible egging @ 8-20, 100-115, 204-220, 270-340: all L. Note says: 3 BUCKETS OF DEBRIS REMOVED FROM LINE | -
318 | COLUMBINE LN | L-4 | C-3A |  | C-3 | 235 | 230.7 | 8 | VCP | 2.51% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 1 | 0 | 0 | 20 | REG3 | UPSTREAM// Localized repair: liner @ 23.9 - 28.0, deposits attached: calcium @ 103.5 M | -
325 | LILAC LN | L-4 | D-8 |  | D-9 | 253.4 | 253.4 | 8 | PVC | 0.4% | 2021 | - | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 7 | 1 | 0 | 20 | REG3 | Sag @ 223.2 water level increase to approx. 40% M | -
353 | W 54TH AVE | L-4 | BR-8A |  | BR-8 | 128 | 127 | 7 | RL | 2.28% | 2021 | - | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | RC3 | Plastic scrap from joint in pipe @ approx. 5', sag @ 121.1 M | 1976 | 48
365 | ALCOTT ST | L-4 | A-3 |  | A-2 | 271 | 268.8 | 8 | CIP | 0.56% | 2021 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 3 | 0 | 0 | 20 | REG3 | Looks lined: liner rough at upstream MH, damage at top of line @ approx. 217.5. Tap 98.8 @ 10 (break-in) w/roots: liner cut in wrong spot so tap is 90% covered/ NEEDS FIXED. Possible sags @ 116-140 L, 153-168 L, 175-182 L, 190-202 M, 220-232 L, 254-266 M. | 1976 | 48
369 | CLAY ST | M-4 | CL-4 |  | CL-3 | 403 | 399.8 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 10 | 0 | 0 | 20 | REG3 | Some deposits attached L. Possible sag 38-396 L | -
370 | CLAY ST | M-4 | CL-3 |  | CL-2 | 388 | 386.8 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 10 | 0 | 0 | 20 | REG3 | Some deposits attached L. Possible sag 325-332 L | -
372 | W 58TH AVE | M-4 | CL-1 |  | BR-1 | 126 | 125.9 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 3 | 0 | 0 | 20 | REG3 | UPSTREAM: Some deposits attached L. Possible sags @ 0-16 L, 22-30 L, 47-65 L, | -
377 | W 58TH AVE | M-4 | BR-1 |  | A-1D | 225 | 224.3 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 4 | 0 | 0 | 20 | REG3 | Slight sag 10-20 L, 34-41 L, 74-84 L, 105-115 L, 217-137 L, 147-167 L, 211-223 M. Some deposits attached L | -
380 | W 52ND PL | L-3 | D-5 |  | D-4 | 225 | 222.8 | 8 | VCP | 2.16% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 5 | 0 | 0 | 20 | REG1 | Crack 155 @ 12 L. Possible infil stain in joint @ 174, 189, 200, 210, 215; no infil observed. Deposits through out L.Point repair PVC @ 203-208. Possible candidate for lining | -
385 | W 52ND AVE | L-3 | D-3A |  | D-3 | 200 | 198.4 | 8 | VCP | 4.69% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 2 | 0 | 0 | 20 | REG1 | Deposits/grease attached throughout but heavy in some spots 72.8 & 92.5-176.4 M Possible candidate for lining | -
387 | W 52ND AVE | L-3 | D-2 |  | D-1 | 21 | 20.5 | 8 | VCP | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | UPSTREAM: Looks like quite a bit of grit. Deposits attached M. Possible candidate for lining | -
390 | ZUNI ST | L-3 | Z-25 |  | Z-24 | 297 | 296.9 | 8 | CIP | 0.6% | 2022 | - | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | Sags @ 28-49 L, 54-75 L, 77-100 L, 114-125 L, 133-142 L, 185-207 L, 221-228 L, 272-294 M. Lined in 2023 | -
395 | ZUNI ST | L-3 | Z-20 |  | Z-19 | 376.3 | 374.1 | 8 | VCP | 4.08% | 2022 | - | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 2 | 0 | 0 | 20 | REG1 | Point repair: PVC @ 176 offset L, unknown object protruding from the bottom of the pipe; not sure if in joint 299/camera can pass over it. | 1973 | 51
400 | EASEMENT | L-3 | T-8G |  | T-8F | 45 | 44.7 | 8 | VCP | 1% | 2023 | 10% | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | Roots in joint @ 9.9 L, sag 12-20 L, Circumferential crack 21.8 L. COULD BE ABANDONED/NO TAPS | 1972 | 52
414 | TEJON ST | L-3 | T-8 |  | T-7 | 311 | 309.1 | 8 | VCP | 0.4% | 2022 | - | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 6 | 0 | 0 | 20 | REG1 | Joint slight offset 15 L, 23 L, 38 L, 52 L, 62 L, 77 L, 106 L, 122 L, 141 L, 162 L, 176 l, 181 L, 208 L, 218 L, 228 L, 239 L, 263 L, 268 L, 274 L. Possible sag @ 30-38 L, 59-66 L, 92-101 L, 119-126 L, 143-151 L, 257-268 L, 280-308 M | 1978 | 46
433 | W 54TH PL | L-3 | U-5 |  | T-4 | 337 | 336.1 | 6 | RL | 2.12% | 2018 | - | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 3 | 0 | 0 | 20 | REG1 | Intruding sealing ring 0.6 L, sag 165-170 L. | 1963 | 61
441 | W 56TH AVE | L-3 | U-1 |  | W-3C | 200 | 399.5 | 8 | VCP | - | 2023 | 5-20% | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 6 | 1 | 0 | 20 | REG1 | SAG 9-30 M, 34-59 M, 77-119 M, 130-151 M, 161-217 M, 225-233.5 L, 290-309 L, 320-328 M, 335-373 L. MATERIAL CHANGE: PVC 393.5 | -
445 | W 55TH AVE | L-3 | V-7B |  | V-7A | 240 | 240.4 | 8 | PVC | 1.06% | 2023 | 5-10% | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 7 | 0 | 0 | 20 | REG1 | Sag 125-142. Egging joints thorughout L. Holding water in the MH V-7A | -
450 | W MOFFAT PL | L-3 | V-4B |  | V-4A | 253 | 249.1 | 8 | PVC | 0.6% | 2022 | - | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 5 | 0 | 0 | 20 | REG1 | Possible sag @ 230-248 L. Joints egged/deformed @ 126 L, 152 L, pipe around tap @ 168 L, 205 L. | -
462 | VALLEJO ST | M-3 | V-2 |  | V-1 | 359 | 357.6 | 8 | PVC | 0.68% | 2022 | - | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | Possible sag @ 29-40 M, 86-95 M, 124-132 L, 138-148 L, 200-210 L, 290-300 L, 325-345 M | -
487 | EASEMENT | M-4 | A-1F |  | A-1G | 338 | 344.9 | 12 | PVC | - | 2023 | 5-15% | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | UPSTREAM; Sag: 0-25 M. | -
501 | EASEMENT | M-3 | PLP-08 |  | PLP-07 | 250 | 250 | 10 | PVC | 0.4% | 2022 | - | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | Infil: runner L (right at the invert for the downstream MH 248.5) | 2020 | 4
509 | EASEMENT | M-3 | Z-10 |  | Z-9 | 130 | 137.1 | 15 | PVC | 8.08% | 2023 | 10% | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | MH Z-9 HAS ROOTS L. Deposits/encrustation throughout pipe L. | -
518 | W 60TH AVE | M-4 | Z-5G |  | Z-5F | 286 | 285.7 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | Sag @ 16-23 L, 195-203 L, 274-283 L. Some grit & rock in the line L | 2016 | 8
521 | W 60TH AVE | N-4 | Z-5D |  | Z-5C | 401 | 401.1 | 8 | PVC | - | 2022 | - | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | Egging/deformed joint @ 163 L. Some grit & rock in the line L | 2016 | 8
523 | W 60TH AVE | N-4 | Z-5B |  | Z-5A | 350 | 350.1 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | Lots of grit; some rock in the line M | 2016 | 8
524 | W 60TH AVE | N-3 | Z-5A |  | Z-5 | 49 | 49.3 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | Lots of grit; some rock in the line M | 2016 | 8
525 | EASEMENT | N-3 | Z-5 |  | Z-4 | 244 | 242.8 | 18 | PVC | 0.35% | 2018 | - | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | REG1 | NO COMMENTS; MH Z-4 looks like it has a grease build up all over the inverts and up the bench M | 1970 | 54
3 | EASEMENT | M-8 | S-28A |  | S-28 | 300 | 300.7 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 10 | REG2 | Some joints throughout egging/deformed L | -
35 | SHERIDAN BLVD | L-8 | S-12G |  | S-12F | 143 | 143.1 | 12 | DIP | 0.3% | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | REG2 | Corrosion thorughout L | -
38 | EASEMENT | L-7 | S-12F-1 |  | S-12F | 90 | 90 | 8 | P.E. | 0.4% | 2023 | 10% | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | REG2 | 73 SEAL IS COMING LOOSE L. Was originally a drop MH but drop wasn't cut out when pipe burst was done. | -
47 | EASEMENT | L-7 | S-10 |  | S-9 | 217 | 217.3 | 12 | VCP | 0.22% | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | REG2 | .7 CRACK CIRC L, EVERY JOINT IS CRACKED RECOMMEND CURE IN PLACE | 1973 | 51
48 | EASEMENT | L-7 | S-9 |  | TN-1 | 258 | 257.1 | 15 | P.E. | 0.2% | 2023 | 5-10% | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | REG2 | 5.2-59 SAG L. Sag: 85-104 L, 145-203 L, 223-257 L | 1973 | 51
52 | STUART ST | L-6 | ST-3 |  | ST-2 | 340 | 340.5 | 8 | VCP | 4.4% | 2023 | 5% | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 10 | H/RC2 | Roots thorughout L | -
74 | TENNYSON ST | L-7 | TN-7 |  | TN-6 | 80 | 79 | 8 | VCP | 6.72% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 1 | 0 | 0 | 10 | REG2 | Deposits attached/encrustation 63-78 L. | -
82 | EASEMENT | L-6 | S-6 |  | S-5 | 360 | 359.5 | 15 | VCP | 0.22% | 2023 | 10% | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | REG2 | Some sagging throughout L | 1973 | 51
87 | RALEIGH ST | L-6 | R-4 |  | R-3 | 30 | 14.9 | 8 | DIP | 12.71% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1 | 0 | 0 | 10 | REG2 | Point repair: PVC 10.3-14.9 END. Tap has Infil coming from connection point M. Corrosion throughout pipe L | 1976 | 48
95 | EASEMENT | L-6 | R-1 |  | Q-1 | 324 | 324.1 | 8 | DIP | 0.4% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | REG2 | Corrosion/deterioration throughout L | 1976 | 48
97 | QUITMAN ST | L-6 | Q-7 |  | Q-6 | 433 | 433.7 | 8 | CIP | 4.2% | 2023 | 5-30% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17 | 0 | 0 | 10 | RC2 | Liner delamination 31.5 L, 310.3 L. | -
98 | QUITMAN ST | L-6 | Q-6 |  | Q-5 | 412 | 400 | 8 | CIP | 3.5% | 2023 | 5-50% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 10 | RC2 | Liner delamination throughout L | -
100 | QUITMAN ST | L-6 | Q-5 |  | Q-3 | 230 | 21 | 8 | DIP | 6.07% | 2023 | 5-10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | RC2 | Corrosion/deterioration throughout pipe L | 1976 | 48
101 | EASEMENT | L-6 | Q-3 |  | Q-2 | 65 | 225.4 | 8 | CIP | 3.3% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 3 | 0 | 0 | 10 | RC2 | Liner delamination 0 L (beginning of pipe) | 1976 | 48
103 | EASEMENT | L-6 | Q-1B |  | Q-1 | 20 | 19.9 | 8 | VCP | 1% | 2015 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG2 | Deposits/encrustation attached throughout L. | -
110 | PERRY ST | L-6 | P-4 |  | P-3 | 37 | 37.6 | 8 | DIP | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 2 | 0 | 0 | 10 | REG2 | Corrosing/deterioration throughtout pipe L. | 1976 | 48
128 | NEWTON ST | L-6 | N-5 |  | N-4 | 330 | 327.3 | 8 | CIP | 2.72% | 2023 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 9 | 0 | 0 | 10 | RC2 | Lined in 2023- Sags: 185-191 L | -
136 | MEADE ST | L-6 | M-5 |  | M-4 | 345 | 343 | 8 | CIP | 3.48% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 9 | 0 | 0 | 10 | REG2 | Possible infil/hole in liner towards top of pipe 216.7 L, 330.9 deposits attached encrustation L | 1964 | 60
137 | MEADE ST | L-6 | M-4 |  | M-3 | 20 | 19 | 8 | VCP | 1% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG2 | Deposits settled/compacted in MH M-4 - 5.6 into line L, deposits/encrustation throughout L, | 1964 | 60
141 | LOWELL BLVD | L-6 | L-8 |  | CC 45A.10 (METRO) | 15 | 20.1 | 8 | PVC | - | 2023 | 5-15% | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 0 | 0 | 10 | REG2 | Sag 6.5-14 L, egging joint/tap 14.1 L | -
148 | W 54TH AVE | L-5 | K-1A |  | K-1 | 241.4 | 245.1 | 8 | VCP | 0.4% | 2023 | 5-10% | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 4 | 0 | 0 | 10 | RC2 | UPSTREAM; Sags 43-56 L, 120-146 L, 157-179 L, 221-238 L | -
150 | W 54TH AVE | L-5 | K-6 |  | K-7 | 10.4 | 12.2 | 8 | VCP | 0.4% | 2023 | 5-20% | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | REG2 | 8.9ft Sag L | -
156 | W 53RD AVE | L-5 | K-4 |  | J-11 | 372.7 | 380.2 | 8 | CIP | 0.4% | 2023 | 5-10% | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 2 | 0 | 0 | 10 | H/RC2 | 201.4ft Sag, Sags: 57-66L, 83-96.3 L, 166-182 L, 198-207 L, 292-304 L. Lined in 2023 after video. | -
193 | W 55TH AVE | L-5 | J-4C |  | J-4B | 322 | 322 | 8 | PVC | 0.4% | 2013 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 7 | 0 | 0 | 10 | RC3 | Sags through out L. | -
224 | EASEMENT | L-5 | G-3D |  | G-3C | 73 | 72.1 | 8 | VCP | 2.2% | 2017 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG3 | Deposits/encrustation attached throughout L. | 1977 | 47
236 | W 55TH PL | L-5 | J-1B |  | L-4H | 246 | 247.4 | 8 | PVC | 2.22% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 3 | 0 | 0 | 10 | REG3 | Material change to steel @ 237.1. Egging: joint @ 71 L, 80.5 (tap) L, 129 L, 208 L. Inside drop @ 246.0. | -
240 | EASEMENT | L-5 | L-4K |  | L-4J | 10 | 7.6 | 8 | PVC | - | 2019 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG3 | Deposits/encrustation attached throughout (grease) L. | -
245 | EASEMENT | L-5 | L-4F |  | L-4E | 215 | 347.4 | 8 | VCP | 0.4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 1 | 0 | 0 | 10 | H1 | UPSTREAM// Deposits/encrustation throughout | 1977 | 47
252 | EASEMENT | L-4 | BE-57 |  | BE-56 | 261 | 264.7 | 10 | P.E. | 0.2% | 2019 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | REG3 | Gauges throughout line. Tap in MH BE-56 | -
253 | EASEMENT | L-4 | BE-56 |  | BE-56A | 102.65 | 102.65 | 10 | P.E. | 0.23% | NEW | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 2 | 0 | 0 | 10 | REG3 | NEW ALIGNMENT; Sag: 11-19 L, 25-47 L, 75-90 L, 97-111 L. | -
256 | EASEMENT | L-4 | BE-56C |  | BE-55 | 260.66 | 260.66 | 10 | P.E. | 0.23% | NEW | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 2 | 0 | 0 | 10 | REG3 | NEW ALIGNMENT; Sags throughout L. | -
268 | EASEMENT | L-4 | DM-3 |  | DM-2 | 290 | 294.4 | 8 | PVC | 0.44% | 2021 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | REG3 | Sag @ approx. 146-157 L, 213-223 L, & 250-263 M from about 5% - 25%. Note on report says: CANT ACCESS D.S. MH DM-2 DUE TO FENCE, CLEANED LINE BACKWARDS NO D.S. DEPTH | 1983 | 41
276 | W 56TH AVE | M-4 | BE-51 |  | BE-50 | 140 | 140.1 | 10 | P.E. | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 1 | 0 | 0 | 10 | REG3 | Deposits/encrustation through out L. Water level is about the same through out the pipe. Note says: 2 BUCKETS OF DEBRIS REMOVED FROM LINE | -
278 | W 56TH AVE | M-4 | BE-49 |  | BE-49A | 363 | 365.8 | 10 | P.E. | 0.23% | 2021 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 0 | 0 | 10 | REG3 | Possible sagging throughout L. | -
309 | COLUMBINE RD | L-4 | C-2D |  | C-2C | 58 | 58 | 8 | VCP | 2% | 2017 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG3 | Deposits/encrustation attached throughout L. | -
335 | COLUMBINE LN | L-4 | C-11 |  | C-10 | 116.2 | 116.2 | 8 | PVC | 0.44% | 2021 | - | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 10 | REG3 | Joint: offset @ 67 L | -
368 | CLAY ST | M-4 | CL-5 |  | CL-4 | 108 | 106.9 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 3 | 0 | 0 | 10 | REG3 | Some deposits attached L. | -
371 | CLAY ST | M-4 | CL-2 |  | CL-1 | 83 | 80.6 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 2 | 0 | 0 | 10 | REG3 | Possible Sag 30-40 L, 70-79 L | -
373 | BRYANT ST | M-4 | BR-5 |  | BR-4 | 111 | 111.4 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 3 | 0 | 0 | 10 | REG3 | UPSTREAM: Some deposits attached L. | -
375 | BRYANT ST | M-4 | BR-3 |  | BR-2 | 399 | 396.8 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 11 | 0 | 0 | 10 | REG3 | Some deposits attached L. | -
376 | BRYANT ST | M-4 | BR-2 |  | BR-1 | 394 | 393.9 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 10 | REG3 | UPSTREAM: Some deposits attached L. | -
379 | W 52ND PL | L-3 | D-6 |  | D-5 | 372 | 369 | 8 | PVC | 4.95% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 8 | 0 | 0 | 10 | REG1 | Some deposits attached L. | -
381 | TEJON ST | L-3 | D-4 |  | D-3 | 278 | 277.8 | 8 | CIP | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 0 | 0 | 10 | REG1 | UPSTREAM: Lined; Possible sag from 0-20 M, 27-42 L, 56-70 L, 76-94 L, 100-125 L, 130-168 L, 247-275 M | -
383 | W 52ND AVE | L-3 | D-3C |  | D-3B | 90 | 88.6 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG1 | Some deposits attachedL. Outside drop @ 88.6 | -
389 | ZUNI ST | L-3 | Z-26 |  | Z-25 | 328 | 324.4 | 8 | VCP | 2.2% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG1 | UPSTREAM: Encrustation/deposits through out L. Possible candidate for lining | -
401 | EASEMENT | L-3 | T-8F |  | T-8E-1 | 126 | 83.1 | 8 | VCP | 2.8% | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 2 | 0 | 0 | 10 | RC1 | Invert in MH T-8F is deteriorated; needs fixed. Crack at tap 19.2 L. | -
425 | VALLEJO ST | L-3 | V-11 |  | V-10 | 101 | 97.8 | 8 | PVC | 10.29% | 2022 |  | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 2 | 0 | 0 | 10 | REG1 | Some deposits attached L. NO COMMENTS | -
428 | W 54TH PL | L-3 | V-9A |  | V-9 | 309 | 309.4 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 7 | 0 | 0 | 10 | REG1 | Possible sag @ 283-289 L. Material change; 305 VCP. | -
434 | TEJON ST | L-3 | T-4 |  | T-3 | 386 | 390.6 | 8 | CIP | 2.72% | 2021 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | REG1 | Sag @ 17-24 L, 139-152 M, 176-183 L, 231-239 L. Deposits in downstream MH (T-3). Lined in 2023 | 1978 | 46
435 | TEJON ST | L-3 | T-3 |  | T-2 | 407 | 415.5 | 8 | PVC | 2.4% | 2019 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 10 | REG1 | Circumferential cracks 1.0 L & 412.6 L. Material change VCP to PVC 0-3.6 & PVC to VCP 411.6-415.5. In good shape aside from the double bends at each end. | 1978 | 46
440 | UMATILLA ST | L-3 | U-2 |  | U-1 | 266 | 264.3 | 8 | VCP | 2.68% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG1 | Spoon wedged in joint @ 150.5; not a significant obstruction. Good candidate for lining. | -
447 | VALLEJO ST | L-3 | V-7 |  | V-4 | 338 | 334.7 | 8 | PVC | 2.4% | 2022 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 7 | 0 | 0 | 10 | REG1 | Possible sag @ 100-105 L, 190-200 L, 250-260 L, 300-310 L, 315-325 L | 1973 | 51
449 | W MOFFAT PL | L-3 | V-4C |  | V-4B | 262 | 260 | 8 | PVC | 1% | 2022 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 6 | 0 | 0 | 10 | REG1 | Possible sag @ 137-147 L, 193-202 L, 252-259 L. | -
474 | EASEMENT | M-4 | Z-13 |  | BE-01 | 126 | 125.6 | 10 | PVC | 3.36% | 2023 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 1 | 0 | 0 | 10 | REG1 | Deposits/grease attached through out L. | -
482 | ALCOTT ST | M-4 | A-1A |  | A-1B | 441 | 439.5 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 8 | 0 | 0 | 10 | REG1 | UPSTREAM: Some deposits attached L. | -
484 | ALCOTT ST | M-4 | A-1C |  | A-1D | 266 | 265.9 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 7 | 0 | 0 | 10 | REG1 | Some deposits attached L. | -
500 | EASEMENT | M-3 | PLP-09 |  | PLP-08 | 268 | 267.9 | 10 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG1 | UPSTREAM: Lot of grit at the end (upstream MH) L | 2020 | 4
515 | EASEMENT | M-3 | Z-6-1 |  | Z-6 | 215 | 213.3 | 18 | PVC | - | 2018 | - | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | REG1 | Possible sag @ 189-210 L | 2016 | 8
520 | W 60TH AVE | M-4 | Z-5E |  | Z-5D | 366 | 365.5 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG1 | Some grit & rock in the line L. Fragments of PVC in line; see no breaks in this line. | 2016 | 8
522 | W 60TH AVE | N-4 | Z-5C |  | Z-5B | 401 | 401 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | REG1 | Grit in the line L | 2016 | 8
1 | EASEMENT | M-8 | STUB |  | S-28B | 5 | 5 | 8 | PVC | - | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
4 | EASEMENT | M-8 | STUB |  | S-28 | 5 | 4 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
6 | SHERIDAN FRONTAGE RD | M-8 | S-27 |  | S-26 | 320 | 315.7 | 8 | VCP | 0.78% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1982 | 42
7 | EASEMENT | M-8 | S-26 |  | S-25 | 34 | 38.1 | 8 | VCP | 0.4% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1982 | 42
8 | EASEMENT | M-8 | S-25 |  | S-24 | 287 | 286.6 | 8 | VCP | 0.4% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1982 | 42
16 | EASEMENT | L-8 | S-19 |  | S-18 | 34 | 33.9 | 10 | PVC | 0.27% | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
17 | SHERIDAN BLVD | L-8 | S-18 |  | S-17 | 140 | 141.3 | 10 | CIP | 0.22% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
25 | W 53RD AVE | L-8 | S-12Q |  | S-12P | 215 | 216.3 | 8 | VCP | 0.36% | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
26 | W 53RD AVE | L-8 | S-12P-1 |  | S-12P | 248 | 246.8 | 8 | CIP | 0.4% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | Lined in 2023. | -
27 | W 53RD AVE | L-8 | S-12P |  | S-12N | 205 | 213 | 8 | VCP | 0.36% | 2023 | 15% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
36 | W 54TH AVE | L-7 | S-12F-3 |  | S-12F-2 | 237 | 236.7 | 8 | CIP | 0.4% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | Surchage from downstream/downstream is flat line that "backs up" into the end of this line. | 1976 | 48
50 | STUART ST | L-6 | ST-5 |  | ST-4 | 42 | 39.8 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
51 | STUART ST | L-6 | ST-4 |  | ST-3 | 65 | 62.7 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 0 | REG2 | NO COMMENTS | -
55 | TENNYSON ST | L-6 | TN-11 |  | TN-10 | 180 | 179.8 | 8 | PVC | 4% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | 1988 | 36
56 | TENNYSON ST | L-6 | TN-10 |  | TN-9 | 20 | 18.3 | 8 | VCP | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
59 | EASEMENT | L-7 | RP-3.4 |  | RP-3.3 | 239 | 236.2 | 8 | PVC | 0.65% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1999 | 25
60 | EASEMENT | L-7 | RP-3.3 |  | RP-3.2 | 67 | 67.2 | 8 | PVC | 0.44% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1999 | 25
61 | EASEMENT | L-7 | RP-3.2 |  | RP-3.1 | 90 | 91.3 | 8 | PVC | 0.94% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1999 | 25
62 | EASEMENT | L-7 | RP-3.1 |  | RP-3 | 174 | 173.3 | 8 | PVC | 1.07% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1999 | 25
63 | EASEMENT | L-7 | STUB |  | RP-6 | 5 | 5 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | H1 | UPSTREAM//NO COMMENTS (televising didn't go to tap but it can be seen from MH) | -
64 | EASEMENT | L-7 | RP-6 |  | RP-5 | 248 | 244.7 | 8 | PVC | 0.36% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 0 | H1 | UPSTREAM//NO COMMENTS | 1999 | 25
65 | EASEMENT | L-7 | RP-5 |  | RP-4 | 42 | 41.9 | 8 | PVC | 0.4% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1999 | 25
66 | EASEMENT | L-7 | RP-4 |  | RP-3 | 138 | 139.3 | 8 | PVC | 0.44% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1999 | 25
67 | EASEMENT | L-7 | RP-3 |  | RP-2 | 32 | 32 | 8 | PVC | 0.71% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1999 | 25
68 | EASEMENT | L-7 | RP-2 |  | RP-1 | 170 | 168.2 | 8 | PVC | 0.42% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1999 | 25
69 | EASEMENT | L-7 | RP-1 |  | TN-8C | 50 | 46.1 | 8 | PVC | 0.24% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1999 | 25
73 | TENNYSON ST | L-7 | TN-8 |  | TN-7 | 55 | 58 | 8 | PVC | 10.47% | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG2 | NO COMMENTS | 2003 | 21
83 | EASEMENT | L-6 | S-5 |  | S-4 | 25 | 25.4 | 15 | VCP | 0.22% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | 1974 | 50
84 | RALEIGH ST | L-6 | STUB |  | R-6 | 5 | 5 | 8 | VCP | 4.44% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | RC2 | (televising didn't go to tap but it can be seen from MH) | -
85 | RALEIGH ST | L-6 | R-6 |  | R-5 | 388 | 388.6 | 8 | CIP | 4.44% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 0 | 0 | RC2 | Lined in 2023 | -
90 | EASEMENT | L-6 | STR-3 |  | STR-2 | 251 | 250.8 | 8 | PVC | - | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
91 | EASEMENT | L-6 | STR-2 |  | STR-1 | 58 | 56 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
96 | QUITMAN ST | L-6 | Q-8 |  | Q-7 | 124 | 123.7 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | REG2 | UPSTREAM: Material change 2: PVC | -
99 | QUITMAN ST | L-6 | Q-5A |  | Q-5 | 30 | 93.9 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
106 | PERRY ST | L-6 | P-7 |  | P-6A | 110 | 107.3 | 8 | VCP | - | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | RC2 | Point repair: PVC 57.2-60. | -
108 | PERRY ST | L-6 | P-6 |  | P-5 | 350 | 350.1 | 8 | CIP | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | H/RC2 | Lined in 2023 after video. | -
109 | PERRY ST | L-6 | P-5 |  | P-4 | 300 | 284.6 | 8 | PVC | 1.21% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
112 | EASEMENT | L-6 | P-2 |  | P-1 | 75 | 75.3 | 8 | PVC | 37.81% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | 2003 | 21
116 | OSCEOLA ST | L-6 | O-5 |  | O-4 | 402 | 401.1 | 8 | CIP | 3.48% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 1 | 0 | 0 | RC2 | UPSTREAM: Lined in 2023 after video. | 1974 | 50
118 | OSCEOLA ST | L-6 | O-3C |  | O-3B | 20 | 32.9 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
119 | OSCEOLA ST | L-6 | O-3B |  | O-3A | 170 | 163.1 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG2 | UPSTREAM: Drop into MH O-3B | -
126 | EASEMENT | L-6 | S-2 |  | S-1 | 300 | 300 | 15 | VCP | 0.22% | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RC2 | NO COMMENTS | 1973 | 51
133 | W 54TH AVE | L-6 | M-1A |  | M-1 | 168 | 169.9 | 8 | VCP | 0.4% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
134 | MEADE ST | L-6 | STUB |  | M-6 | 10 | 10 | 8 | VCP | 3.68% | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 |  | -
146 | KING ST | L-5 | K-3 |  | K-2 | 322 | 321.3 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
147 | KING ST | L-5 | K-2 |  | K-1 | 326 | 333.9 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
149 | W 54TH AVE | L-5 | K-1 |  | K-6 | 130 | 131.7 | 8 | VCP | 0.4% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
157 | EASEMENT | L-5 | L-6C-3 |  | L-6C-2 | 60 | 79.5 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
158 | EASEMENT | L-5 | L-6C-2 |  | L-6C-1 | 213 | 211.5 | 8 | PVC | - | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
162 | W 55TH AVE | L-5 | L-6B-3 |  | L-6B-2 | 75 | 78.3 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
163 | EASEMENT | L-5 | L-6B-2 |  | L-6B-1 | 200 | 212.2 | 8 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | -
167 | LOWELL BLVD | L-6 | CC 45A.8 (METRO) |  | L-6 | 50 | 14.5 | 12 | PVC | 0.8% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | 1978 | 46
169 | LOWELL BLVD | L-6 | LH-3 |  | LH-2 | 95 | 94 | 8 | PVC | 2% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | REG2 | UPSTREAM//NO COMMENTS | 2007 | 17
170 | LOWELL BLVD | L-6 | LH-2 |  | LH-1 | 110 | 110.5 | 8 | PVC | 6.81% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | 2007 | 17
173 | LOWELL BLVD | L-6 | L-5 |  | L-4 | 182 | 105.3 | 8 | CIP | - | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
174 | LOWELL BLVD | L-6 | L-4 |  | L-3 | 182 | 44.3 | 8 | PVC | - | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
175 | EASEMENT | L-6 | L-3 |  | L-2 | 6 | 37.3 | 8 | PVC | - | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG2 | NO COMMENTS | -
176 | JULIAN ST | L-5 | J-12 |  | J-11 | 193 | 287.5 | 8 | PVC | 7.3% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
177 | W 53RD AVE | L-5 | J-11 |  | J-10 | 12 | 10.9 | 8 | VCP | 7.3% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RC3 | NO COMMENTS | -
178 | W 53RD AVE | L-5 | J-10 |  | J-9 | 47.4 | 47.4 | 8 | VCP | 4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RC3 | NO COMMENTS | -
180 | W 53RD PL | L-5 | J-8A |  | J-8 | 247 | 245.2 | 8 | VCP | 0.4% | 2018 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
181 | JULIAN ST | L-5 | J-8 |  | J-7 | 154 | 153.3 | 8 | VCP | 3.8% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 2 | 0 | 0 | REG3 | NO COMMENTS | -
185 | IRVING ST | L-5 | I-3 |  | I-2 | 325.1 | 326.1 | 8 | CIP | - | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 0 | 0 | REG3 | Lined in 2023 after video. | -
188 | W 54TH AVE | L-5 | I-1 |  | J-6A | 206.7 | 207.4 | 8 | VCP | 1% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
192 | W 55TH AVE | L-5 | STUB |  | J-4C | 6 | 6.2 | 8 | VCP | - | 2014 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
195 | W 55TH AVE | L-5 | J-4A |  | J-4 | 83 | 81.6 | 8 | DIP | 0.94% | 2013 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | UPSTREAM; Point repair: PVC 0-17. Point repair: PVC 66-80. | -
197 | JULIAN ST | L-5 | J-3 |  | J-2 | 28 | 27.1 | 8 | VCP | 1.8% | 2013 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1976 | 48
199 | W 55TH PL | L-5 | J-1B |  | J-1A | 250 | 250.7 | 8 | PVC | 1.96% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
202 | W 55TH PL | L-5 | L-5B |  | L-5A | 223 | 223.9 | 8 | CIP | 7.43% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | Lined in 2023 | 1978 | 46
204 | W 53RD AVE | L-5 | G-6D-3 |  | G-6D-2 | 154.5 | 151.3 | 8 | PVC | 6.14% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2021 | 3
205 | W 53RD AVE | L-5 | G-6D-2 |  | G-6D-1 | 64.1 | 60.2 | 8 | PVC | 5.04% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2021 | 3
206 | W 53RD AVE | L-5 | G-6D-1 |  | G-6D | 60.8 | 54.7 | 8 | PVC | 0.57% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2021 | 3
207 | W 53RD AVE | L-5 | G-6D |  | G-6C | 25 | 23.4 | 8 | VCP | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
208 | REGIS RD | L-5 | G-6C2 |  | G-6C1 | 143 | 141.7 | 8 | PVC | 1% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1988 | 36
209 | REGIS RD | L-5 | G-6C1 |  | G-6C | 237.7 | 237.7 | 8 | PVC | 2% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1988 | 36
210 | W 53RD AVE | L-5 | G-6C |  | G-6B | 134 | 135 | 8 | VCP | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
220 | W 54TH AVE | L-5 | G-3H |  | G-3G | 52 | 51.6 | 8 | PVC | 0.4% | 2018 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | NO COMMENTS | 1983 | 41
221 | W 54TH AVE | L-5 | G-3G |  | G-3F | 149 | 148.5 | 8 | PVC | 0.4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1983 | 41
227 | W 55TH AVE | L-5 | STUB |  | G-3A | 10 | 10 | 8 | VCP | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 |  | -
230 | W 55TH PL | L-5 | STUB |  | G-2B | 10 | 10 | 8 | VCP | 0.4% | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
231 | W 55TH PL | L-5 | G-2B |  | G-2A1 | 134 | 131.5 | 8 | VCP | 0.4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
234 | W 55TH PL | L-5 | G-2 |  | G-1 | 15 | 14.8 | 8 | PVC | 0.4% | 2013 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1977 | 47
238 | EASEMENT | L-5 | STUB |  | L-4L | 10 | 10 | 8 | PVC | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 |  | -
254 | EASEMENT | L-4 | BE-56A |  | BE-56B | 166.67 | 166.67 | 8 | PVC | 0.11% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NEW LINE | -
255 | EASEMENT | L-4 | BE-56B |  | BE-56C | 152 | 152.29 | 8 | PVC | 0.14% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NEW LINE | -
257 | W 56TH AVE | L-4 | BE-55 |  | DM-1 | 21 | 19.5 | 10 | P.E. | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
258 | EASEMENT | L-4 | DM-9 |  | DM-8 | 133 | 132.3 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
259 | EASEMENT | L-4 | DM-8 |  | DM-7 | 56 | 54.6 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
260 | EASEMENT | L-4 | ELM-1 |  | ELM-2 | 255 | 258.9 | 8 | PVC | 2.35% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2002 | 22
261 | EASEMENT | L-4 | ELM-2 |  | DM-7 | 160 | 160.5 | 8 | PVC | 4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2002 | 22
264 | W 55TH AVE | L-4 | DM-5B |  | DM-5A | 269 | 270.5 | 8 | PVC | 1.66% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1983 | 41
265 | W 55TH AVE | L-4 | DM-5A |  | DM-5 | 271 | 270.4 | 8 | PVC | 1.89% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1983 | 41
266 | EASEMENT | L-4 | DM-5 |  | DM-4 | 201 | 202 | 8 | PVC | 3.09% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1983 | 41
267 | EASEMENT | L-4 | DM-4 |  | DM-3 | 56 | 56 | 8 | PVC | 0.54% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1983 | 41
272 | CLAY ST | M-4 | BE-52C |  | BE-52B | 397 | 399.7 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
273 | CLAY ST | M-4 | BE-52B |  | BE-52A | 242 | 245.1 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
277 | W 56TH AVE | M-4 | BE-50 |  | BE-49 | 264 | 262.5 | 10 | P.E | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
279 | W 56TH AVE | M-4 | BE-49A |  | BE-49B | 18 | 16.4 | 10 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
280 | W 56TH AVE | L-5 | STUB: BE-49B |  | BE-49B | 255 | 254.9 | 8 | VCP | 0.68% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
281 | EASEMENT | OUT OF DISTRICT | AR-2G |  | AR-2F | 45 | 45 | 8 | PVC | 5.83% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
282 | EASEMENT | OUT OF DISTRICT | AR-2F |  | AR-2E | 90.5 | 90.5 | 8 | PVC | 4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
283 | EASEMENT | OUT OF DISTRICT | AR-2E |  | AR-2D | 57.5 | 57.5 | 8 | PVC | 2% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
284 | EASEMENT | OUT OF DISTRICT | AR-2D |  | AR-2C | 65.6 | 65.6 | 8 | PVC | 2% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
285 | EASEMENT | OUT OF DISTRICT | AR-2C |  | AR-2B | 58.3 | 58.3 | 8 | PVC | 2% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
286 | EASEMENT | OUT OF DISTRICT | AR-2B |  | AR-2A | 76 | 76 | 8 | PVC | 1.81% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
287 | EASEMENT | OUT OF DISTRICT | AR-2A |  | AR-2 | 91.7 | 91.7 | 8 | PVC | 2% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
288 | W 53RD AVE | OUT OF DISTRICT | AR-10 |  | AR-9 | 30.2 | 30.2 | 8 | PVC | 3.67% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
289 | W 53RD AVE | OUT OF DISTRICT | AR-9 |  | AR-8 | 43.5 | 43.5 | 8 | PVC | 2.11% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
290 | W 53RD AVE | OUT OF DISTRICT | AR-8 |  | AR-7 | 53.9 | 53.9 | 8 | PVC | 2.11% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
291 | W 53RD AVE | OUT OF DISTRICT | AR-7 |  | AR-6 | 79 | 79 | 8 | PVC | 2.11% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
292 | EASEMENT | OUT OF DISTRICT | AR-6E |  | AR-6D | 125 | 125 | 8 | PVC | 0.6% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
293 | EASEMENT | OUT OF DISTRICT | AR-6D |  | AR-6C | 78 | 78 | 8 | PVC | 0.6% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
294 | EASEMENT | OUT OF DISTRICT | AR-6C |  | AR-6B | 74 | 74 | 8 | PVC | 0.6% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
295 | EASEMENT | OUT OF DISTRICT | AR-6B |  | AR-6A | 43 | 43 | 8 | PVC | 0.6% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
296 | EASEMENT | OUT OF DISTRICT | AR-6A |  | AR-6 | 50 | 50 | 8 | PVC | 0.6% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
297 | EASEMENT | OUT OF DISTRICT | AR-6 |  | AR-5 | 37.9 | 37.9 | 8 | PVC | 2.11% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
298 | EASEMENT | OUT OF DISTRICT | AR-5 |  | AR-4 | 117.7 | 117.7 | 8 | PVC | 3.43% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
299 | EASEMENT | OUT OF DISTRICT | AR-4 |  | AR-3 | 99.6 | 99.6 | 8 | PVC | 1.54% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
300 | EASEMENT | OUT OF DISTRICT | AR-3 |  | AR-2 | 101.7 | 101.7 | 8 | PVC | 1.49% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
301 | PRIMROSE LN | OUT OF DISTRICT | AR-2 |  | AR-1 | 161.2 | 161.2 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
302 | PRIMROSE LN | L-4 | AR-1 |  | C-2B-2 | 187.4 | 187.4 | 6 | PVC | 5.5% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | 2018 | 6
303 | PRIMROSE LN | L-4 | C-2B-2 |  | C-2B-1 | 290 | 288.4 | 8 | PVC | 4.15% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
304 | PRIMROSE LN | L-4 | C-2B-1 |  | C-2B | 83 | 82.1 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
305 | COLUMBINE RD | L-4 | C-2F |  | C-2E-1 | 61 | 59 | 8 | PVC | 2% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
306 | COLUMBINE RD | L-4 | C-2E-1 |  | C-2E | 59 | 58.2 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
307 | COLUMBINE RD | L-4 | C-2E |  | C-2D-1 | 128.8 | 128.8 | 8 | VCP | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | REG3 | NO COMMENTS | -
308 | COLUMBINE RD | L-4 | C-2D-1 |  | C-2D | 96.9 | 96.9 | 8 | VCP | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | RC3 | NO COMMENTS | -
310 | W 54TH AVE | L-4 | STUB |  | C-2C | 10 | 10 | 8 | VCP | 4% | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 |  | -
311 | W 54TH AVE | L-4 | C-2C |  | C-2B | 266 | 259.9 | 8 | CIP | 4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | Lined in 2023 | -
312 | W 54TH AVE | L-4 | C-2B-4 |  | C-2B-3 | 121 | 120.4 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
313 | W 54TH AVE | L-4 | C-2B-3 |  | C-2B | 352 | 354.5 | 8 | PVC | 1.26% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
314 | PRIMROSE LN | L-4 | C-2B |  | C-2A-2 | 48.6 | 48.6 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1991 | 33
315 | PRIMROSE LN | L-4 | C-2A-2 |  | C-2A-1 | 191.7 | 191.7 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1991 | 33
316 | PRIMROSE LN | L-4 | C-2A-1 |  | C-2A | 160 | 158.4 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1991 | 33
317 | PRIMROSE LN | L-4 | C-2A |  | C-2 | 332.4 | 332.4 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | REG3 | NO COMMENTS | 1991 | 33
319 | CLAY ST | L-4 | STUB |  | C-3 | 10 | 10 | 8 | VCP | 6.67% | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 |  | -
320 | CLAY ST | L-4 | C-3 |  | C-2 | 249 | 245.1 | 8 | CIP | 6.67% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 2 | 0 | 0 | REG3 | Lined in 2023 | -
321 | CLAY ST | L-4 | C-2 |  | C-1 | 235 | 236.5 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
322 | W 55TH AVE | L-4 | C-1 |  | BR-6-A | 224 | 225.3 | 8 | PVC | 0.4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
323 | W 55TH AVE | L-4 | BR-6A |  | BR-6 | 135.7 | 135.7 | 8 | PVC | 0.4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
324 | LILAC LN | L-4 | D-7 |  | D-8 | 254.5 | 254.5 | 8 | PVC | 0.4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
326 | COLUMBINE RD | L-4 | D-9 |  | C-8A | 13 | 12.3 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
327 | COLUMBINE RD | L-4 | STUB |  | C-8B | 6 | 6 | 8 | VCP | - | 2014 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | NO COMMENTS | -
328 | COLUMBINE RD | L-4 | C-8B |  | C-8A | 176 | 174.7 | 8 | VCP | 0.4% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | RC3 | NO COMMENTS | 1973 | 51
330 | COLUMBINE LN | L-4 | STUB:C-15 |  | C-15 | 8 | 8 | 8 | PVC | - | 2014 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
331 | COLUMBINE LN | L-4 | C-15 |  | C-14 | 51 | 58.1 | 8 | PVC | 0.93% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
332 | COLUMBINE LN | L-4 | C-14 |  | C-13 | 152.8 | 152.8 | 8 | PVC | 0.86% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
333 | COLUMBINE LN | L-4 | C-13 |  | C-12 | 27.3 | 27.3 | 8 | PVC | 0.81% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
334 | COLUMBINE LN | L-4 | C-12 |  | C-11 | 147 | 144.2 | 8 | PVC | 0.53% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
336 | COLUMBINE LN | L-4 | C-10 |  | C-9 | 91 | 90.1 | 8 | PVC | 0.39% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
337 | COLUMBINE LN | L-4 | C-9 |  | C-8 | 57 | 56.1 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
338 | EASEMENT | L-4 | C-8 |  | C-5E | 104 | 103 | 8 | PVC | 0.56% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
339 | EASEMENT | L-4 | C-5E |  | C-5D | 12.8 | 12.8 | 8 | PVC | 1.46% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
340 | EASEMENT | L-4 | C-5D |  | C-5C | 40.3 | 40.3 | 8 | PVC | 1.03% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
342 | ROSEMARY LN | L-4 | C-5B-1 |  | C-5B | 239.6 | 239.6 | 8 | PVC | 0.5% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
343 | ROSEMARY LN | L-4 | C-5B |  | C-5A | 63.8 | 63.8 | 8 | PVC | 0.9% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
344 | ROSEMARY LN | L-4 | C-5A |  | C-5 | 203 | 200.7 | 8 | PVC | 0.8% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
345 | COLUMBINE LN | L-4 | STUB:C-7 |  | C-7 | 22.7 | 22.7 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
346 | COLUMBINE LN | L-4 | C-7 |  | C-6 | 126 | 124.9 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
347 | COLUMBINE LN | L-4 | C-6 |  | C-5 | 128.6 | 128.6 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
348 | COLUMBINE LN | L-4 | C-5 |  | C-4 | 337 | 334.9 | 8 | PVC | 2.32% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
349 | W 54TH AVE | L-4 | C-4 |  | BR-8-1 | 202 | 200.2 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
350 | W 54TH AVE | L-4 | BR-8-1 |  | BR-8 | 23 | 20.1 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
351 | ROSEMARY LN | L-4 | STUB |  | BR-8B | 10 | 10 | 8 | VCP | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 |  | -
355 | BRYANT ST | L-4 | BR-7 |  | BR-6 | 331 | 327.8 | 8 | CIP | 4.6% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | Lined in 2023 | 1976 | 48
358 | BEACH CT | L-4 | STUB:B-2 |  | B-2 | 151 | 151 | 8 | VCP | 6.92% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | RC3 | NO COMMENTS | -
361 | W 54TH AVE | L-4 | A-5A |  | A-5 | 147.1 | 147.1 | 8 | PVC | 1.58% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
362 | ALCOTT ST | L-4 | A-5 |  | A-4 | 257.2 | 257.2 | 8 | PVC | 4.73% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | REG3 | Inside drop in A-4. A-4 has cracks and a hole under stairs that have roots coming through L. | -
363 | ALCOTT ST | L-4 | A-4 |  | A-3 | 401 | 405 | 8 | PVC | 4.71% | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | RC3 | NO COMMENTS | -
367 | W 56TH AVE | M-4 | A-1 |  | A-1A | 160 | 157 | 8 | PVC | - | 2021 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
374 | BRYANT ST | M-4 | BR-4 |  | BR-3 | 146 | 145 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | REG3 | NO COMMENTS | -
382 | W 52ND AVE | L-3 | D-3D |  | D-3C | 121 | 120.6 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG1 | NO COMMENTS | -
388 | ZUNI ST | L-3 | STUB |  | Z-26 | 10 | 10 | 8 | VCP | 2.2% | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 |  | -
393 | ZUNI ST | L-3 | Z-22 |  | Z-21 | 330 | 327.8 | 8 | CIP | 7.2% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | REG1 | Lined in 2023 | 1973 | 51
396 | ZUNI ST | L-3 | Z-19 |  | Z-18 | 25 | 23.4 | 8 | VCP | 4.08% | 2018 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 1973 | 51
398 | EASEMENT | L-3 | STUB |  | T-8H | 5 | 5 | 8 | PVC | - | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | (televising didn't go into stub but end can be seen from MH, not taps) | -
399 | EASEMENT | L-3 | T-8H |  | T-8G | 98 | 95.7 | 8 | PVC | 1% | 2023 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS. COULD BE ABANDONED/NO TAPS | 1972 | 52
402 | EASEMENT | L-3 | T-8E-4 |  | T-8E-3 | 127 | 125.3 | 8 | PVC | 0.75% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2019 | 5
403 | EASEMENT | L-3 | T-8E-3 |  | T-8E-2 | 190 | 189.3 | 8 | PVC | 0.75% | 2023 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2019 | 5
404 | EASEMENT | L-3 | T-8E-2 |  | T-8E-1 | 51 | 51.2 | 8 | PVC | 0.75% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS | 2019 | 5
407 | W 53RD AVE | L-3 | T-8D |  | T-8C | 347 | 342 | 8 | VCP | 3.8% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | RC1 | Lined from 317-321. NO COMMENTS. Possible candidate for lining | 1978 | 46
408 | VALLEJO WAY | L-3 | STUB |  | T-8C2 | 10 | 10 | 8 | PVC | * | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS | -
409 | VALLEJO ST | L-3 | T-8C2 |  | T-8C1 | 60 | 69.5 | 8 | PVC | * | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS | -
410 | VALLEJO ST | L-3 | T-8C1 |  | T-8C | 200 | 268.6 | 8 | PVC | * | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 2 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS | -
411 | W 53RD AVE | L-3 | T-8C |  | T-8B | 172 | 173.8 | 8 | VCP | 2.6% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS | 1978 | 46
418 | W 53RD PL | L-3 | W-6A |  | W-6 | 253 | 251.6 | 8 | CIP | 2.39% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | REG1 | Lined in 2023 | -
423 | VALLEJO ST | L-3 | STUB |  | V-12 | 5 | 5 | 8 | PVC | * | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | NO COMMENTS/NOT VIDEOED TO END | -
424 | VALLEJO ST | L-3 | V-12 |  | V-11 | 180 | 185.8 | 8 | PVC | 1.4% | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 0 | REG1 | NO COMMENTS | -
427 | W 54TH PL | L-3 | V-9B |  | V-9A | 253 | 252.2 | 8 | PVC | 0.06% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | REG1 | UPSTREAM: NO COMMENTS | -
431 | UMATILLA ST | L-3 | U-7 |  | U-6 | 84 | 84 | 8 | RL | 0.64% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS | -
438 | UMATILLA ST | L-3 | U-4 |  | U-3 | 378 | 377.5 | 8 | VCP | 2.68% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | REG1 | NO COMMENTS. Good candidate for lining. | -
439 | UMATILLA ST | L-3 | U-3 |  | U-2 | 265 | 262.2 | 8 | VCP | 2.68% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | REG1 | NO COMMENTS. Good candidate for lining. | -
442 | W 56TH AVE | M-3 | W-3C |  | W-3B | 220 | 219.3 | 12 | PVC | 0.25% | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 0 | 0 | REG1 | NO COMMENTS | -
444 | W 55TH AVE | L-3 | STUB:V-7B |  | V-7B | 52 | 52.2 | 8 | PVC | - | 2014 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG1 | UPSTREAM; Drop into MH V-7B. Material change: DIP 50.3. NO COMMENTS | -
446 | W 55TH AVE | L-3 | V-7A |  | V-7 | 300 | 316.4 | 8 | PVC | 0.4% | 2023 | 5-10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | REG1 | NO COMMENTS | -
448 | W MOFFAT PL | L-3 | V-4 |  | V-4A | 92 | 91.1 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | REG1 | NO COMMENTS | 1973 | 51
452 | W 56TH AVE | M-3 | W-3B |  | W-3 | 275 | 54.7 | 12 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | -
453 | W 56TH AVE | M-3 | STUB:W-3A |  | W-3A | 50 | 20.4 | 6 | PVC | - | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS | -
454 | W 56TH AVE | M-3 | W-3A |  | W-3 | 190 | 207.8 | 8 | PVC | 0.96% | 2023 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | REG1 | OUTSIDE DROP AT 203.5 | 1991 | 33
459 | VALLEJO ST | M-3 | V-3 |  | V-3A | 71 | 68.1 | 8 | PVC | - | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG1 | NO COMMENTS; DUPLICATE ON 12/7/22 | -
460 | VALLEJO ST | M-3 | V-3A |  | V-2 | 291 | 287.3 | 8 | PVC | 0.68% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG1 | NO COMMENTS; DUPLICATE ON 12/7/22 | -
466 | ZUNI ST | M-3 | Z-16 |  | Z-15 | 291 | 289.6 | 10 | PVC | 3% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG1 | NO COMMENTS | 1970 | 54
467 | W 57TH AVE | M-3 | STUB |  | Z-15A | 3 | 3 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0 | 0 | REG1 | NO COMMENTS | -
468 | W 57TH AVE | M-3 | Z-15A |  | Z-15 | 242 | 242.3 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 0 | 0 | REG1 | NO COMMENTS | 1970 | 54
469 | ZUNI ST | M-3 | Z-15 |  | Z-14 | 269 | 266.7 | 10 | PVC | 1.88% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | REG1 | NO COMMENTS | 1970 | 54
470 | W 58TH AVE | M-3 | STUB |  | Z-14A | 5 | 5 | 8 | VCP | 0.6% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG1 | UPSTREAM: Capped with bricks | -
472 | ZUNI ST | M-3 | Z-14 |  | Z-13 | 260 | 257.2 | 10 | PVC | 0.52% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG1 | NO COMMENTS | 1970 | 54
473 | W 59TH AVE | M-3 | Z-12 |  | Z-13 | 333 | 330.7 | 8 | PVC | 0.52% | 2018 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | REG1 | UPSTREAM: NO COMMENTS | -
475 | ZUNI CT | M-4 | BE-07 |  | BE-06 | 347 | 347.1 | 8 | PVC | 2.41% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
476 | ZUNI CT | M-4 | BE-06 |  | BE-05 | 348 | 347.5 | 8 | PVC | 1.14% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
477 | ZUNI CT | M-4 | BE-05 |  | BE-04 | 377 | 376.5 | 8 | PVC | 1.13% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
478 | EASEMENT | M-4 | BE-04 |  | BE-03 | 154 | 152.9 | 8 | PVC | 1.55% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
479 | EASEMENT | M-4 | BE-03 |  | BE-02 | 136 | 136 | 8 | PVC | 3.85% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
480 | EASEMENT | M-4 | BE-02 |  | BE-01 | 67 | 66.2 | 8 | PVC | 2.78% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
481 | EASEMENT | M-4 | BE-01 |  | A-1H | 65 | 64.6 | 12 | PVC | 3.36% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
485 | EASEMENT | M-4 | A-1D |  | A-1E | 244 | 180.9 | 8 | PVC | - | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | -
486 | EASEMENT | M-4 | A-1E |  | A-1F | 160 | 158.4 | 12 | PVC | - | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS | -
488 | EASEMENT | M-4 | A-1G |  | A-1H | 22 | 22.8 | 12 | PVC | - | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | UPSTREAM//NO COMMENTS | -
489 | W 59TH PL | M-3 | A1-H |  | Z-10 | 276 | 275.5 | 15 | PVC | - | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | -
491 | EASEMENT | M-3 | Z-11 |  | PLP-02 | 13 | 13.1 | 12 | PVC | 5% | 2023 | 5% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | Inside drop 9.1 | 2020 | 4
492 | EASEMENT | M-3 | PLP-17 |  | PLP-16 | 268 | 268.2 | 8 | PVC | 3.7% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
493 | EASEMENT | M-3 | PLP-16 |  | PLP-11 | 226 | 225.7 | 8 | PVC | 3.24% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
494 | EASEMENT | M-3 | PLP-15 |  | PLP-14 | 266 | 266.4 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
495 | EASEMENT | M-3 | PLP-14 |  | PLP-13 | 270 | 270.1 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
496 | EASEMENT | M-3 | PLP-13 |  | PLP-12 | 155 | 155.3 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
497 | EASEMENT | M-3 | PLP-12 |  | PLP-11 | 321 | 321 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
498 | EASEMENT | M-3 | PLP-11 |  | PLP-10 | 317 | 317.3 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
499 | EASEMENT | M-3 | PLP-10 |  | PLP-09 | 333 | 333 | 8 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
502 | EASEMENT | M-3 | PLP-07 |  | PLP-06 | 15 | 14.5 | 10 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | UPSTREAM: NO COMMENTS | 2020 | 4
503 | EASEMENT | M-3 | PLP-06 |  | PLP-05 | 249 | 248.8 | 10 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
504 | EASEMENT | M-3 | PLP-05 |  | PLP-04 | 128 | 127.5 | 10 | PVC | 0.4% | 2022 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2020 | 4
505 | EASEMENT | M-3 | PLP-04 |  | PLP-03 | 170 | 170 | 10 | PVC | 0.4% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NEW LINE | 2020 | 4
506 | EASEMENT | M-3 | PLP-03 |  | PLP-02 | 178 | 178 | 10 | PVC | 0.4% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NEW LINE | 2020 | 4
507 | EASEMENT | M-3 | PLP-02 |  | PLP-01 | 80 | 80 | 12 | PVC | 0.4% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NEW LINE | 2020 | 4
508 | EASEMENT | M-3 | PLP-01 |  | Z-10 | 77 | 77 | 12 | PVC | 0.4% | NEW | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NEW LINE | 2020 | 4
510 | EASEMENT | M-3 | Z-9 |  | Z-8 | 200 | 194.7 | 15 | DIP | 1.08% | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | 190-195 MATERIAL CHANGE TO PVC. | 2016 | 8
511 | EASEMENT | M-3 | Z-8 |  | Z-7-2 | 55 | 54.8 | 18 | PVC | - | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | OUTSIDE DROP 48.8’ | 2016 | 8
512 | EASEMENT | M-3 | Z-7-2 |  | Z-7-1 | 208 | 207.5 | 18 | PVC | - | 2023 | 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2016 | 8
513 | EASEMENT | M-3 | Z-7-1 |  | Z-7 | 155 | 154.7 | 18 | PVC | - | 2023 | 15% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2016 | 8
514 | EASEMENT | M-3 | Z-7 |  | Z-6-1 | 102 | 104 | 18 | PVC | - | 2023 | 15% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 2016 | 8
527 | EASEMENT | N-3 | Z-3 |  | Z-2 | 281 | 280.8 | 18 | PVC | 0.3% | 2018 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 1970 | 54
528 | EASEMENT | N-3 | Z-2 |  | Z-1 | 312 | 308.1 | 18 | PVC | 0.3% | 2023 | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | REG1 | NO COMMENTS | 1970 | 54
[5 empty] | Totals- | 103262.58 | 102351.37 |  |  | Average |  |  | 25.1562 | 22.7273 | 14.0659 | 12.377 | 14.8718 | 12.3846 | 11.0989 | 11.039 | 1283 | 104 | 0 | 18.3081
[5 empty] | Number of lines | 529 | [6 empty] | 64 | 11 | 91 | 61 | 156 | 130 | 91 | 77
[5 empty] | Lines Done | 521